## R-series
[12 empty] | Version 7.3 | [11 empty] | Version 7.3
Airfi: air handling unit selection program | [12 empty] | Calculation of annual efficiency for exhaust air heat recovery
Project:
Name: | [9 empty] | 1
Project:
Select model: | [12 empty] | Name: |  |  |  |  | = insert value
Airfi-Model 53mini Electric | [12 empty] | Calculation parameters: |  |  |  | Outdoor air temperature [°C] | Percentage of the year | Exhaust air temperature | Supply air temperature | SS,Kd | ST,Kd | SJ,Kd
Power supply: Electric plug 230 V, 50 Hz, 10 A, max 1165 W | [12 empty] | Supply air volume flow, through heat recovery | qtLTO | 25 | dm3/s | -32 | 0% | -6.5 | -2.3611 | 0 | 0 | 0
[13 empty] | Extract air volume flow, through heat recovery | qpLTO | 26.9444 | dm3/s | -31 | 0% | -6.5 | -1.3611 | 0 | 0 | 0
[13 empty] | Supply air to extract air ratio for volume flow through heat recovery |  |  |  | -30 | 0% | -6.5 | -0.36111 | 0 | 0 | 0
[14 empty] | RLTO | 0.92784 |  | -29 | 0% | -6.5 | 0.63889 | 0 | 0 | 0
[17 empty] | -28 | 0% | -6.5 | 1.6389 | 0 | 0 | 0
[13 empty] | Additional extract air flow rate included in heat recovery requirements |  |  |  | -27 | 0% | -6.5 | 2.6389 | 0 | 0 | 0
[14 empty] | qep1 | 0 | dm3/s | -26 | 0% | -6.5 | 3.6389 | 0 | 0 | 0
[13 empty] | Operational time of the additional extract air | Tqep1 | 0 | h / day | -25 | 0% | -6.5 | 4.6389 | 0 | 0 | 0
[13 empty] | Supply / extract air volume flow ratio for entire ventilation system |  |  |  | -24 | 0% | -6.5 | 5.6389 | 0 | 0 | 0
[14 empty] | RT | 0.92784 |  | -23 | 0% | -6.5 | 6.6389 | 0 | 0 | 0
[17 empty] | -22 | 0% | -6.5 | 7.6389 | 0 | 0 | 0
[13 empty] | Heat recovery cell efficiency (EN 308) | η | 81.65% |  | -21 | 0% | -6.5 | 8.6389 | 0 | 0 | 0
[13 empty] | Supply side temperature ratio for balanced air flow (EN 13141-7) | ηt(RLTO=1) | 80.35% |  | -20 | 0% | -6.5 | 9.6389 | 0 | 0 | 0
[13 empty] | Supply side temperature ratio | ηt(RLTO) | 83.35% |  | -19 | 0% | -6.5 | 10.6389 | 0 | 0 | 0
[17 empty] | -18 | 0% | -6.5 | 11.6389 | 0 | 0 | 0
[13 empty] | Select climate zone (city) |  |  |  | -17 | 0% | -6.5 | 12.6389 | 0 | 0 | 0
[13 empty] | Indoor temperature | ts | 21 | °C | -16 | 0% | -6.5 | 13.6389 | 0 | 0 | 0
[13 empty] | Minimum exhaust air temperature | tj,min | -6.5 | °C | -15 | 0% | -6.5 | 14.6389 | 0 | 0 | 0
[13 empty] | Supply air temperature limitation |  |  |  | -14 | 0% | -6.0685 | 15.1738 | 0 | 0 | 0
[13 empty] | Maximum supply air temperature in a limited situation | tt,max | 20 | °C | -13 | 0% | -5.2951 | 15.3403 | 0 | 0 | 0
[17 empty] | -12 | 0.03425% | -4.5217 | 15.5067 | 4.125 | 3.4383 | 3.1902
[13 empty] | Annual efficiency | ηₐ | 77.34% |  | -11 | 0.137% | -3.7483 | 15.6732 | 12 | 10.0025 | 9.2806
[17 empty] | -10 | 0.4909% | -2.9749 | 15.8397 | 40.0417 | 33.3762 | 30.9676
|  | 25 |  | 26.9444 | [8 empty] | Total energy demand for ventilation |  | 3443.2785 | kWh/a | -9 | 0.6735% | -2.2016 | 16.0061 | 20 | 16.6708 | 15.4677
[13 empty] | Recovered heating energy |  | 2662.9814 | kWh/a | -8 | 0.9132% | -1.4282 | 16.1726 | 25.375 | 21.151 | 19.6247
Operating point (insert air flow and pressure difference values): | [6 empty] | Boost situation calculation: | [5 empty] | Electricity consumption of fans and electronics |  | 330.6971 | kWh/a | -7 | 1.13% | -0.65479 | 16.3391 | 22.1667 | 18.4768 | 17.1434
|  | Supply air |  | Extract air |  |  | Maximum boost reserve: |  | Supply air | Extract air | [6 empty] | -6 | 2.386% | 0.11859 | 16.5055 | 123.75 | 103.1503 | 95.7064
Air volume flow: |  | 90 | m³/h | 97 | m³/h |  |  |  | 118% | 121.1% | [6 empty] | -5 | 4.292% | 0.89198 | 16.672 | 180.9167 | 150.8009 | 139.9183
|  | 25 | dm³/s | 26.9444 | dm³/s | [11 empty] | -4 | 5.685% | 1.6654 | 16.8384 | 127.0833 | 105.9287 | 98.2844
Pressure difference: |  | 100 | Pa | 100 | Pa |  | Insert the desired boost value: | [9 empty] | -3 | 8.094% | 2.4387 | 17.0049 | 211 | 175.8764 | 163.1843
[7 empty] | Boost value [%]: |  |  | 10% | [6 empty] | -2 | 11.11% | 3.2121 | 17.1714 | 253 | 210.885 | 195.6665
|  | Supply fan: |  | Extract fan: | [12 empty] | -1 | 15.72% | 3.9855 | 17.3378 | 370.3333 | 308.6868 | 286.4104
Control voltage: |  | 4.621 | V | 4.3915 | V |  | Operating point in boost situation: | [9 empty] | 0 | 21.26% | 4.7589 | 17.5043 | 424.375 | 353.7325 | 328.2054
Fan power: |  | 16.6957 | W | 16.6551 | W |  |  |  | Supply air | Extract air | [6 empty] | 1 | 24.16% | 5.5323 | 17.6708 | 211.6667 | 176.4321 | 163.6999
[7 empty] | Air volume flow: |  | 99 | 106.7 | m³/h | [5 empty] | 2 | 30.03% | 6.3057 | 17.8372 | 407.7083 | 339.8402 | 315.3157
Total power: | 37.7508 | W | [6 empty] | 27.5 | 29.6389 | dm³/s | [5 empty] | 3 | 34.85% | 7.0791 | 18.0037 | 316.5 | 263.8147 | 244.7765
SFP: | 1.4011 | kW/(m³/s) | SFPint : | - | W/(m³/s) |  | Pressure difference: |  | 121 | 121 | Pa | [5 empty] | 4 | 40.25% | 7.8524 | 18.1701 | 335.0417 | 279.2698 | 259.1163
SPI: | 0.38918 | W/(m³/h) | SFPint_limit : | - | W/(m³/s) |  | Control voltage: |  | 5.015 | 4.4707 | V | [5 empty] | 5 | 44.12% | 8.6258 | 18.3366 | 226 | 188.3795 | 174.7851
Note: The above values also include the device's electronics. | [16 empty] | 6 | 46.19% | 9.3992 | 18.5031 | 113.125 | 94.2939 | 87.4892
[17 empty] | 7 | 50.45% | 10.1726 | 18.6695 | 217.5833 | 181.3639 | 168.2758
Sound power levels in connection ducts | [16 empty] | 8 | 54.59% | 10.946 | 18.836 | 196.625 | 163.8943 | 152.0669
Connection duct | Sound power levels in octave bands LW,oct [dB] | [8 empty] | LWtot [dB] | LWAtot [dB] | [5 empty] | 9 | 58.04% | 11.7194 | 19.0025 | 151 | 125.8642 | 116.7812
| 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz |  | 4 kHz | 8 kHz | [7 empty] | 10 | 62.18% | 12.4928 | 19.1689 | 166.375 | 138.6798 | 128.672
Supply air | 74.2158 | 68.2158 | 63.2158 | 56.2158 | 54.2158 | 48.2158 |  | 39.2158 | 26.2158 | 75.549 | 60.2158 | [5 empty] | 11 | 64.63% | 13.2661 | 19.3354 | 89.5833 | 74.6711 | 69.2824
Outdoor air | 64.3929 | 58.3929 | 48.3929 | 38.3929 | 28.3929 | 21.3929 |  | 16.3929 | 21.3929 | 65.4622 | 45.3929 | [5 empty] | 12 | 69.67% | 14.0395 | 19.5018 | 165.375 | 137.8463 | 127.8986
Extract air | 62.4915 | 59.4915 | 50.4915 | 38.4915 | 34.4915 | 20.4915 |  | 14.4915 | 20.4915 | 64.4505 | 46.4915 | [8 empty] | Total | 4410.75 | 3676.5261 | 3411.2098
Exhaust air | 72.7853 | 67.7853 | 62.7853 | 57.7853 | 55.7853 | 48.7853 |  | 39.7853 | 28.7853 | 74.4653 | 60.7853
Kitchen bypass* | 68.1531 | 64.4678 | 59.0972 | 51.9972 | 49.3972 | 38.8825 |  | 29.6678 | 25.0531 | 70.1704 | 55.693 | [5 empty] | SI,Kd = heating degree days, between indoor air and outdoor air, Kd
* With kitchen bypass, the total extract air volume flow is larger than the inserted value
Sound power levels through casing: | [16 empty] | SS,Kd = heating degree days, between supply air and outdoor air, Kd
| Sound power levels in octave bands LW,oct [dB] | [8 empty] | LWtot [dB] | LWAtot [dB]
| 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz |  | 4 kHz | 8 kHz | [7 empty] | SE,Kd = heating degree days, between exhaust air and outdoor air, Kd
Through casing | 49.3743 | 45.3743 | 40.3743 | 27.3743 | 20.3743 | 13.3743 |  | 9.3743 | 6.3743 | 51.2268 | 34.3743
Sound pressure level in a room with an absorption area of 10m²: | [9 empty] | LpA,10m²Sab [dB] | 30.3949
Sound pressure level in a typical bathroom (V < 10 m³) with an absorption area < 2-3 m²: | [9 empty] | LpA,<3m²Sab [dB] | 36.4155
Specific energy consumption (SEC) and classification | [8 empty] | Class | SEC-value
According to Commission Regulations (EU) No 1253/2014 & No 1254/2014 | [8 empty] | A+ | SEC < -42
NB! SEC-calculation is only used for air handling units intended for residential buildings | [7 empty] | ► | A | -42 < SEC < -34
Reference air flow: | 226.8 | [7 empty] | B | -34 < SEC < -26
Calculation parameters: | [8 empty] | C | -26 < SEC < -23 |  |  | All rights reserved. | www.airfi.fi | www.airfi.eu
General typology |  |  |  | SEC-value |  | -39.0477 |  |  | D | -23 < SEC < -20 |  |  | Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program.
Ventilation control |  |  |  | [kWh / (a·m2)] |  |  |  |  | E | -20 < SEC < -10
Motor & drive |  |  |  | Class |  | A |  |  | F | -10 < SEC < 0 |  |  | The selection program is made by Insinööritoimisto W. Zenner Oy. The program is based on laboratory measurements according to SFS-EN 13141-7.
Climate | [8 empty] | G | SEC > 0
All rights reserved. |  | www.airfi.fi | www.airfi.eu
Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program.
The selection program is made by Insinööritoimisto W. Zenner Oy. The program is based on laboratory measurements according to SFS-EN 13141-7.
Dimensioning of heating coil |  |  |  | Not available for selected model
Insert parameters:
Start by inserting either inlet or outlet water temperature
Inlet air temperature |  |  | 1 | ºC | Heating coil dimensioning by inlet water temperature
Outlet air temperature |  |  | 20 | ºC | Inlet water temperature |  |  |  |  | - | ºC
Inlet water temperature |  |  | 50 | ºC | Outlet water temperature |  |  |  |  | - | ºC
Outlet water temperature |  |  | 30 | ºC | Volume flow |  |  |  |  | - | dm3/s
[5 empty] | Heating coil fluid side pressure loss |  |  |  |  | - | kPa
Supply air volume flow |  |  | 25 | dm3/s | Control valve pressure loss* |  |  |  |  | - | kPa
Required heating power |  |  | - | W | Flow velocity |  |  |  |  | - | m/s
Heating coil dimensioning by outlet water temperature
[5 empty] | Inlet water temperature |  |  |  |  | - | ºC
[5 empty] | Outlet water temperature |  |  |  |  | - | ºC
[5 empty] | Volume flow |  |  |  |  | - | dm3/s
[5 empty] | Heating coil fluid side pressure loss |  |  |  |  | - | kPa
*Using Oras DN15S Radiator valve body & Stabila radiator valve (fully open, CV = 1.00) |  |  |  |  | Control valve pressure loss* |  |  |  |  | - | kPa
[5 empty] | Flow velocity |  |  |  |  | - | m/s
Version 7.3
FI
ENG
SVE
GER
Supply air
Extract air
Sound insulated casing: "dB-paketti" (NB! Requires a cabinet)
Post heating water
POL
EST
LAT
LTU

## Tulokset (hidden)
[53 empty] | dB-ruksittu |  | FALSE | dB Package | [39 empty] | Tuloilman rajoituksen ehdot kielivalinnasta riippuen (v.5.8 ja 5.9)
[28 empty] | KIELIVALINTA | [24 empty] | Model 60, 100, 130 ja 53mini |  | TRUE |  | Ei valintamahdollisuutta Model 150:lle, v4.4 (18.11.2019), eikä model 250 ja 350 | [38 empty] | Kielivalinta |  |  |  | 1
|  | Model 60 | [19 empty] | Liukuvalinta | [5 empty] | Kielivalinta ja sen vaikutus syöttösoluihin | [5 empty] | Kielen valinnan vaikutus käyrien tulostukseen (dm³/s vai m³/h) | [18 empty] | Valinta |  | FALSE | [40 empty] | FALSE | Suomi |  |  | 21
|  | Model 100 | [19 empty] | 1 | [5 empty] | 2 | Valittu kieli |  |  |  |  | Yläakseli: |  | Air volume flow [dm³/s] | [59 empty] | TRUE | Muut kielet
|  | 7 | Valinta, huom. Numerot muutettu siten että koneet suuruusjärjestyksessä | [18 empty] | Muutettu laskentaohjelman järjestysnumeroksi | [11 empty] | Ala-akseli: |  | Air volume flow [m³/h] | [18 empty] | dB Package vaimennus
[22 empty] | 7 | [5 empty] | FALSE | Suomi | [25 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
|  | Ilmamääräkäyrät | [25 empty] | TRUE | Muut kielet |  |  |  |  | Ilmamääräkäyrät | [19 empty] | Vaimennus | 8 | 3 | 5 | 4 | 3 | 3 | 5 | 3 | [26 empty] | Tehostuksen piirto |  |  |  | Kielivalinnan vaikutus |  |  | Kielivalinta tuloilman lämpötilarajoitukseen
|  | Tulo | [10 empty] | Poisto | [8 empty] | Muokattu koneet suuruusjärjestykseen | [11 empty] | Tulo | [8 empty] | Poisto | [9 empty] | a-painotus | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | [22 empty] | Tehostusvara |  |  |  |  | Tuloilma | l/s | Pa |  | Tuloilma | l/s | Pa | Suomi | Muut |  | Valinta | Lukema
|  | 10 V | 0 | 7 V | 0 | 6 V | 0 | 4V | 0 |  |  |  | 10 V | 0 | 7 V | 0 | 6 V | 0 | 4V | 0 | [7 empty] | m³/h | [5 empty] | 10 V |  | 7 V |  | 6 V |  | 4V |  |  | 10 V |  | 7 V |  | 6 V |  | 4V | [34 empty] | Haluttu tehostus |  |  |  |  | Origo | 1 | 0.16 |  | Origo | 3.6 | 0.16 | 17 | 21 |  | 21 | 21
| 10V dm³/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  |  | 10V dm³/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  | Liukuvalinta |  | Laskentaohjelma |  |  |  | dm³/s | [5 empty] | Pa | m³/h | Pa | m³/h | Pa | m³/h | Pa | m³/h |  | Pa | m³/h | Pa | m³/h | Pa | m³/h | Pa | m³/h | [33 empty] | 10% |  |  |  |  | Mitoitus | 25 | 100 |  | Mitoitus | 90 | 100 | 18 | 22 |  | 22 | 22
| 95.3803 | 25 | 95.3803 | 10 | 84.0396 | 10 | 69.5264 | 10 | 40.0158 |  |  | 103.5755 | 15 | 103.5755 | 10 | 98.8637 | 10 | 81.983 | 10 | 48.7976 |  | 1 | Model 53mini | 7 | [9 empty] | 25 | 343.3691 | 10 | 302.5424 | 10 | 250.2951 | 10 | 144.0569 |  | 15 | 372.8719 | 10 | 355.9095 | 10 | 295.1388 | 10 | 175.6714 |  |  |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | LpA10m2 | LpA2,5m2 | [23 empty] | Tehostus | 27.5 | 121 |  | Tehostus | 99 | 121 | 19 | 23 |  | 23 | 23
| 88.9477 | 120 | 88.9477 | 40 | 80.2259 | 25 | 67.2972 | 20 | 37.7479 |  |  | 94.8809 | 120 | 94.8809 | 40 | 94.8637 | 25 | 79.6966 | 20 | 46.4153 |  | 2 | Model 60 | 1 |  |  |  | Mitoituspisteen tilavuusvirrat dm³/s | [5 empty] | 120 | 320.2118 | 40 | 288.8131 | 25 | 242.2699 | 20 | 135.8925 |  | 120 | 341.5712 | 40 | 341.5095 | 25 | 286.9076 | 20 | 167.0952 |  |  | Model 60 | 41.5975 | 42.5975 | 35.5975 | 27.5975 | 20.5975 | 14.5975 | 5.5975 | 6.5975 | 45.6806 | 31.5171 | 27.5377 | 33.5583 | [18 empty] | Halutun tehostuksen toimintapiste: |  |  |  |  | Poistoilma | l/s | Pa |  | Poistoilma | l/s | Pa | 20 | 24 |  | 24 | 24
| 83.7627 | 190 | 83.7627 | 60 | 77.5674 | 35 | 65.7582 | 40 | 32.617 |  |  | 88.808 | 190 | 88.808 | 60 | 92.0681 | 35 | 78.1228 | 60 | 34.6466 |  | 3 | Model 100 | 2 |  |  |  | Tulo | Poisto |  |  |  |  | 190 | 301.5456 | 60 | 279.2426 | 35 | 236.7296 | 40 | 117.4212 |  | 190 | 319.7087 | 60 | 331.4452 | 35 | 281.242 | 60 | 124.7277 |  |  | Model 100 | 43.1891 | 43.1891 | 36.1891 | 27.1891 | 19.1891 | 13.1891 | 5.1891 | 3.1891 | 46.6719 | 31.7677 | 27.7883 | 33.8089 |  |  |  |  | Keittiöohitus valinta |  |  | Tekstit | [10 empty] | (Toisen potenssin verkkokäyrästä suoraan): |  |  |  |  | Origo | 2 | 0.55096 |  | Origo | 7.2 | 0.55096 | 21 | 25 |  | 25 | 25
| 78.9265 | 250 | 78.9265 | 80 | 74.8033 | 55 | 62.5355 | 50 | 29.6194 |  |  | 83.4021 | 250 | 83.4021 | 80 | 89.1541 | 55 | 74.8411 | 80 | 25.6685 |  | 4 | Model 130 | 6 |  |  |  | 25 | 26.9444 |  |  |  |  | 250 | 284.1352 | 80 | 269.2917 | 55 | 225.1279 | 50 | 106.6299 |  | 250 | 300.2476 | 80 | 320.9547 | 55 | 269.428 | 80 | 92.4067 |  |  | Model 150 | 49.2145 | 44.2145 | 44.2145 | 34.2145 | 22.2145 | 20.2145 | 15.2145 | 14.2145 | 51.4366 | 37.8685 | 33.8891 | 39.9097 | Poistettu Model 150 dB-paketti mahdollisuus18.11.2019 |  |  |  | TRUE |  |  | Kitchen bypass* |  | * With kitchen bypass, the total extract air volume flow is larger than the inserted value | [8 empty] | Tulo | Poisto |  |  |  | Mitoitus | 26.9444 | 100 |  | Mitoitus | 97 | 100
| 72.6742 | 320 | 72.6742 | 100 | 71.9198 | 140 | 45.3908 | 70 | 21.9159 |  |  | 76.8313 | 320 | 76.8313 | 100 | 86.1052 | 180 | 46.4366 | 82 | 24.4583 |  | 5 | Model 150 | 3 | [9 empty] | 320 | 261.627 | 100 | 258.9112 | 140 | 163.4068 | 70 | 78.8973 |  | 320 | 276.5927 | 100 | 309.9787 | 180 | 167.1718 | 82 | 88.0497 |  |  | Model 250 | 53.5243 | 47.5243 | 38.5243 | 25.5243 | 21.5243 | 17.5243 | 17.5243 | 16.5243 | 54.6158 | 35.5243 | 31.5449 | 37.5655 | Ei Model 250:ssä | [6 empty] | Kitchen bypass |  | * Not available for the selected model | [8 empty] | 27.5 | 29.6389 | l/s |  |  | Tehostus | 29.6389 | 121 |  | Tehostus | 106.7 | 121
| 67.6569 | 370 | 67.6569 | 200 | 54.9175 | 175 | 34.6092 |  |  |  |  | 71.942 | 370 | 71.942 | 270 | 48.0489 | 200 | 38.257 |  |  |  | 6 | Model 250 | 4 | [9 empty] | 370 | 243.565 | 200 | 197.7032 | 175 | 124.5932 |  |  |  | 370 | 258.9912 | 270 | 172.9759 | 200 | 137.7252 |  |  |  |  | Model 350 | 53.5243 | 47.5243 | 38.5243 | 25.5243 | 21.5243 | 17.5243 | 17.5243 | 16.5243 | 54.6158 | 35.5243 | 31.5449 | 37.5655 | Ei Model 350:ssä | [5 empty] | Valinta | Kitchen bypass* |  | * With kitchen bypass, the total extract air volume flow is larger than the inserted value | [8 empty] | 121 | 121 | Pa | [15 empty] | Vesimalli
| 58.105 | 450 | 58.105 | 260 | 40.7241 | [6 empty] | 62.6626 | 460 | 62.6626 | 280 | 43.7182 | [5 empty] | 7 | Model 350 | 5 | [9 empty] | 450 | 209.1779 | 260 | 146.6068 | [5 empty] | 460 | 225.5852 | 280 | 157.3855 | [6 empty] | Model 130 | 38.2227 | 42.2227 | 34.2227 | 26.2227 | 18.2227 | 12.2227 | 6.2227 | 1.2227 | 44.2285 | 30.3571 | 26.3777 | 32.3983 | [17 empty] | Vesipatteri | [18 empty] | FALSE
[53 empty] | Model 53mini | 41.3743 | 42.3743 | 35.3743 | 23.3743 | 17.3743 | 10.3743 | 4.3743 | 3.3743 | 45.4074 | 30.4572 | 26.4778 | 32.4984 | [17 empty] | FALSE | 99 | 106.7 | m³/h
[14 empty] | Vanha | Äänet | [68 empty] | 27.5 | 29.6389 | dm³/s |  | Max tehostus |  | Tarkistus |  | Ohjausjännite
|  |  | Tulopuhallin |  |  | Poistopuhallin |  |  | Elektroniikka |  |  |  |  | Kennon | Tulokanava | [9 empty] | Ulkokanava | [9 empty] | Poistokanava | [9 empty] | Jätekanava | [9 empty] | Vaipan läpi | [14 empty] | Keittiöohitus | [9 empty] | SFPint | SFPint_limit | Malli, teksti | Sähkönsyöttö, teksti |  |  |  |  | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto |  |  | LTO-hyötysuhteet v6.0 eteenpäin | [5 empty] | Jälkilämmityspatterin
|  |  | Tarkistus | Ohjaus | Teho | Tarkistus | Ohjaus | Teho | Teho | Total teho | SFP | Vert qV | SFP vert | hyötys | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | LpA10m2 | LpA2,5m2 |  |  |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | - | - | Airfi-Model 60 Electric | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | Model 60 |  |  |  | 94.12% | 100.8% | TRUE | TRUE | 5.1399 | 4.8863 | [6 empty] | EN 13141-7 | EN 308 | ottoteho
1 |  | Model 60 | TRUE | 4.7416 | 15.2462 | TRUE | 4.5065 | 15.2242 | 4.4 | 34.8705 | 1.2942 | 63 | 1.1865 | 0.795 | 82.9951 | 65.9951 | 61.9951 | 58.9951 | 52.9951 | 50.9951 | 45.9951 | 37.9951 | 83.1392 | 61.9951 | 73.5805 | 56.5805 | 53.5805 | 44.5805 | 34.5805 | 28.5805 | 20.5805 | 17.5805 | 73.7147 | 50.5805 | 73.6542 | 54.6542 | 49.6542 | 46.6542 | 40.6542 | 33.6542 | 24.6542 | 18.6542 | 73.7367 | 50.6542 | 80.8369 | 64.8369 | 62.8369 | 55.8369 | 52.8369 | 50.8369 | 45.8369 | 41.8369 | 81.037 | 60.8369 | 49.5975 | 45.5975 | 40.5975 | 31.5975 | 23.5975 | 17.5975 | 10.5975 | 9.5975 | 51.4818 | 35.5975 | 31.6181 | 37.6387 |  |  | Model 60 | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 54.9195 | - | - | Airfi-Model 100 Electric | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | Model 100 |  |  |  | 88.9% | 97.45% | TRUE | TRUE | 5.3749 | 5.0277 |  |  | 1 |  | Model 60 |  | - | - | 920
2 |  | Model 100 | TRUE | 4.9821 | 16.8363 | TRUE | 4.6522 | 15.4596 | 4.4 | 36.6959 | 1.3619 | 63 | 1.2159 | 0.825 | 83.5412 | 68.5412 | 60.5412 | 57.5412 | 51.5412 | 49.5412 | 43.5412 | 33.5412 | 83.7127 | 61.5412 | 71.6221 | 60.6221 | 53.6221 | 42.6221 | 30.6221 | 24.6221 | 16.6221 | 11.6221 | 72.0228 | 50.6221 | 67.183 | 58.183 | 51.183 | 43.183 | 35.183 | 29.183 | 19.183 | 14.183 | 67.8119 | 48.183 | 83.4807 | 67.4807 | 64.4807 | 57.4807 | 52.4807 | 50.4807 | 43.4807 | 39.4807 | 83.6579 | 61.4807 | 51.1891 | 46.1891 | 41.1891 | 31.1891 | 22.1891 | 16.1891 | 10.1891 | 6.1891 | 52.7361 | 36.1891 | 32.2097 | 38.2303 |  |  | Model 100 | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 54.9195 | - | - | Airfi-Model 150 Electric | Electric plug 230 V, 50 Hz, 16 A, max 2200 W | Model 150 |  |  |  | 173.2% | 210.9% | TRUE | TRUE | 3.7501 | 3.6492 |  |  | 2 |  | Model 100 |  | - | - | 920
3 |  | Model 150 | FALSE | 3.4623 | 13.883 | FALSE | 3.3416 | 11.8371 | 4.4 | 30.1201 | 1.1179 | 112 | 1.1879 | 0.795 | 55.4569 | 54.4985 | 49.8814 | 40.0495 | 30.9867 | 30.558 | 20.4391 | 15.6134 | 58.71 | 44.617 | 61.1958 | 54.4763 | 48.9445 | 39.3791 | 24.8574 | 20.1071 | 13.8455 | 8.8455 | 62.2656 | 44.064 | 59.1402 | 58.9437 | 54.2767 | 39.7188 | 29.141 | 22.7252 | 17.8308 | 13.8308 | 62.7477 | 48.0495 | 59.4838 | 59.2871 | 58.3193 | 47.197 | 37.2089 | 36.2612 | 26.8103 | 20.9558 | 63.9413 | 51.8565 | 49.2145 | 44.2145 | 44.2145 | 34.2145 | 22.2145 | 20.2145 | 15.2145 | 14.2145 | 51.4366 | 38.2145 | 34.2351 | 40.2557 |  |  | Model 150 | - | - | - | - | - | - | - | - | - | - | - | - | Airfi-Model 250 Electric | Electric plug 230 V, 50 Hz, 16 A, max 3500 W | Model 250 |  |  |  | 90.98% | 91.94% | TRUE | TRUE | 4.561 | 4.5856 |  |  | 3 |  | Model 150 |  | - | - | 1840
4 |  | Model 250 | FALSE | 4.1973 | 23.8021 | FALSE | 4.2384 | 22.2623 | 4.4 | 50.4643 | 1.8729 | 175 | 1.0568 | 79.5% | 62.2805 | 64.2805 | 55.2805 | 52.2805 | 51.2805 | 46.2805 | 42.2805 | 40.2805 | 67.0593 | 56.2805 | 54.1062 | 52.1062 | 40.1062 | 34.1062 | 30.1062 | 25.1062 | 15.1062 | 10.1062 | 56.3752 | 39.1062 | 55.1606 | 52.1606 | 39.1606 | 35.1606 | 30.1606 | 25.1606 | 16.1606 | 7.1606 | 57.0376 | 39.1606 | 61.3063 | 61.3063 | 52.3063 | 49.3063 | 48.3063 | 43.3063 | 39.3063 | 37.3063 | 64.8574 | 53.3063 | 53.5243 | 47.5243 | 38.5243 | 25.5243 | 21.5243 | 17.5243 | 17.5243 | 16.5243 | 54.6158 | 35.5243 | 31.5449 | 37.5655 |  |  | Model 250 | - | - | - | - | - | - | - | - | - | - | 201.3811 | 1267.6333 | Airfi-Model 350 Electric | Electric plug 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Model 350 |  |  |  | 157.1% | 151.9% | TRUE | TRUE | 4.561 | 4.5856 |  |  | 4 |  | Model 250 |  | - | - | 2380
5 |  | Model 350 | FALSE | 4.1973 | 23.8021 | FALSE | 4.2384 | 22.2623 | 4.4 | 50.4643 | 1.8729 | 194.4444 | 1.1718 | 79.5% | 62.2805 | 64.2805 | 55.2805 | 52.2805 | 51.2805 | 46.2805 | 42.2805 | 40.2805 | 67.0593 | 56.2805 | 54.1062 | 52.1062 | 40.1062 | 34.1062 | 30.1062 | 25.1062 | 15.1062 | 10.1062 | 56.3752 | 39.1062 | 55.1606 | 52.1606 | 39.1606 | 35.1606 | 30.1606 | 25.1606 | 16.1606 | 7.1606 | 57.0376 | 39.1606 | 61.3063 | 61.3063 | 52.3063 | 49.3063 | 48.3063 | 43.3063 | 39.3063 | 37.3063 | 64.8574 | 53.3063 | 53.5243 | 47.5243 | 38.5243 | 25.5243 | 21.5243 | 17.5243 | 17.5243 | 16.5243 | 54.6158 | 35.5243 | 31.5449 | 37.5655 |  |  | Model 350 | - | - | - | - | - | - | - | - | - | - | - | - | Airfi-Model 130 Electric | Electric plug 230 V, 50 Hz, 10 A, max 1255 W | Model 130 |  |  |  | 121.6% | 124.2% | TRUE | TRUE | 5.0083 | 4.8024 |  |  | 5 |  | Model 350 |  | - | - | 7140
6 |  | Model 130 | TRUE | 4.602 | 15.9533 | TRUE | 4.3697 | 14.6591 | 4.4 | 35.0124 | 1.2994 | 91 | 1.5171 | 0.775 | 69.3997 | 68.3997 | 61.3997 | 56.3997 | 51.3997 | 50.3997 | 44.3997 | 34.3997 | 72.485 | 59.3997 | 58.7116 | 55.7116 | 48.7116 | 41.7116 | 33.7116 | 27.7116 | 19.7116 | 10.7116 | 60.8208 | 44.7116 | 56.8514 | 54.8514 | 47.8514 | 42.8514 | 39.8514 | 32.8514 | 21.8514 | 13.8514 | 59.4544 | 45.8514 | 67.4915 | 65.4915 | 61.4915 | 55.4915 | 51.4915 | 49.4915 | 42.4915 | 32.4915 | 70.4793 | 58.4915 | 46.2227 | 45.2227 | 39.2227 | 30.2227 | 21.2227 | 15.2227 | 11.2227 | 4.2227 | 49.2833 | 34.2227 | 30.2432 | 36.2638 |  |  | Model 130 | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 54.9195 | - | - | Airfi-Model 53mini Electric | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | Model 53mini |  |  |  | 118% | 121.1% | TRUE | TRUE | 5.015 | 4.4707 |  |  | 6 |  | Model 130 |  | - | - | 920
7 |  | Model 53mini | TRUE | 4.621 | 16.6957 | TRUE | 4.3915 | 16.6551 | 4.4 | 37.7508 | 1.4011 | 63 | 1.443 | 0.797 | 74.2158 | 68.2158 | 63.2158 | 56.2158 | 54.2158 | 48.2158 | 39.2158 | 26.2158 | 75.549 | 60.2158 | 64.3929 | 58.3929 | 48.3929 | 38.3929 | 28.3929 | 21.3929 | 16.3929 | 21.3929 | 65.4622 | 45.3929 | 62.4915 | 59.4915 | 50.4915 | 38.4915 | 34.4915 | 20.4915 | 14.4915 | 20.4915 | 64.4505 | 46.4915 | 72.7853 | 67.7853 | 62.7853 | 57.7853 | 55.7853 | 48.7853 | 39.7853 | 28.7853 | 74.4653 | 60.7853 | 49.3743 | 45.3743 | 40.3743 | 27.3743 | 20.3743 | 13.3743 | 9.3743 | 6.3743 | 51.2268 | 34.3743 | 30.3949 | 36.4155 |  |  | Model 53mini | 68.1531 | 64.4678 | 59.0972 | 51.9972 | 49.3972 | 38.8825 | 29.6678 | 25.0531 | 70.1704 | 55.693 | [16 empty] | 7 |  | Model53mini |  | 80.35% | 81.65% | 920
Hyötysuhteet A. Pulkkasen mailista 20.2.2019 (Model 60,100,150)
Huom. Päivitetty v6.0 lähtien
[14 empty] | Huom. Yllä olevia arvoja käytetään SEC-laskennassa, vaikka hyvin pieni poikkeama mitoituspisteen laskentaohjelman arvoissa voi olla | [40 empty] | Huom. Valinta erilainen kuin aiemmat sarakkeet vasemmalla
|  |  | Tulopuhallin |  |  | Poistopuhallin |  |  | Elektroniikka | [5 empty] | Tulokanava | [9 empty] | Ulkokanava | [9 empty] | Poistokanava | [9 empty] | Jätekanava | [9 empty] | Vaipan läpi | [14 empty] | Keittiöohitus | [13 empty] | Tehostuksen toimintapiste |  |  |  | Max tehostus |  | Tarkistus |  | Ohjausjännite |  |  | Tehostus positiivinen luku
|  |  | Tarkistus | Ohjaus | Teho | Tarkistus | Ohjaus | Teho | Teho | Total | SFP | Vert qV | SFP vert | Hyötys. | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | LpA10m2 | LpA2,5m2 | SEC | Class |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | SFPint | SFPint_limit |  | Sähkönsyöttö, teksti | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto | [6 empty] | EN 13141-7 | EN 308
|  | Valinta | TRUE | 4.621 | 16.6957 | TRUE | 4.3915 | 16.6551 | 4.4 | 37.7508 | 1.4011 | 63 | 1.443 | 0.797 | 74.2158 | 68.2158 | 63.2158 | 56.2158 | 54.2158 | 48.2158 | 39.2158 | 26.2158 | 75.549 | 60.2158 | 64.3929 | 58.3929 | 48.3929 | 38.3929 | 28.3929 | 21.3929 | 16.3929 | 21.3929 | 65.4622 | 45.3929 | 62.4915 | 59.4915 | 50.4915 | 38.4915 | 34.4915 | 20.4915 | 14.4915 | 20.4915 | 64.4505 | 46.4915 | 72.7853 | 67.7853 | 62.7853 | 57.7853 | 55.7853 | 48.7853 | 39.7853 | 28.7853 | 74.4653 | 60.7853 | 49.3743 | 45.3743 | 40.3743 | 27.3743 | 20.3743 | 13.3743 | 9.3743 | 6.3743 | 51.2268 | 34.3743 | 30.3949 | 36.4155 | -39.0477 | A |  | 68.1531 | 64.4678 | 59.0972 | 51.9972 | 49.3972 | 38.8825 | 29.6678 | 25.0531 | 70.1704 | 55.693 | - | - | Airfi-Model 53mini Electric | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | 99 | 106.7 | 121 | 121 | 118% | 121.1% | TRUE | TRUE | 5.015 | 4.4707 |  | TRUE | Valinta |  | Model53mini |  | 0.80346 | 0.81646 | 920
[84 empty] | 27.5 | 29.6389
|  | Tulosteeseen |  | 4.621 | 16.6957 |  | 4.3915 | 16.6551 |  | 37.7508 | 1.4011 | 63 | 1.443 | 0.797 | 74.2158 | 68.2158 | 63.2158 | 56.2158 | 54.2158 | 48.2158 | 39.2158 | 26.2158 | 75.549 | 60.2158 | 64.3929 | 58.3929 | 48.3929 | 38.3929 | 28.3929 | 21.3929 | 16.3929 | 21.3929 | 65.4622 | 45.3929 | 62.4915 | 59.4915 | 50.4915 | 38.4915 | 34.4915 | 20.4915 | 14.4915 | 20.4915 | 64.4505 | 46.4915 | 72.7853 | 67.7853 | 62.7853 | 57.7853 | 55.7853 | 48.7853 | 39.7853 | 28.7853 | 74.4653 | 60.7853 | 49.3743 | 45.3743 | 40.3743 | 27.3743 | 20.3743 | 13.3743 | 9.3743 | 6.3743 | 51.2268 | 34.3743 | 30.3949 | 36.4155 | -39.0477 | A |  | 68.1531 | 64.4678 | 59.0972 | 51.9972 | 49.3972 | 38.8825 | 29.6678 | 25.0531 | 70.1704 | 55.693 | - | - | Airfi-Model 53mini Electric | Power supply: Electric plug 230 V, 50 Hz, 10 A, max 1165 W | 99 | 106.7 | 121 | 121 | 118% | 121.1% |  |  | 5.015 | 4.4707 |  |  | Tulosteeseen |  |  |  | 0.80346 | 0.81646 | 920
|  | T | [81 empty] | 27.5 | 29.6389
|  |  | Vesipatteri |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | Valittuna | FALSE | [5 empty] | Model 250 | Model 350 |  |  |  | Tulosteeseen |  |  |  |  | SPI
|  |  | Menoveden lämpötila |  |  | - | - | - | 50 | 50 | - | - |  | - | - |  | Tulosteeseen |  | 0.38918
|  |  | Paluuveden lämpötila |  |  | - | - | - | -5.0297 | -15.4661 | - | - |  | - | -
|  |  | Virtaama |  |  | - | - | - | 0.0024745 | 0.00208 | - | - |  | - | -
|  |  | Painehäviö patt |  |  | - | - | - | 0.017953 | 0.010445 | - | - |  | - | -
|  |  | Painehäviö ventt |  |  | - | - | - | 0.0079353 | 0.0056069 | - | - |  | - | -
|  |  | Virtausnopeus |  |  | - | - | - | 0.020164 | 0.016949 | - | - |  | - | -
[5 empty] | Virhe |  |  |  | TRUE | TRUE |  |  |  | 0
|  |  | Menoveden lämpötila |  |  | - | - | - | 14.9703 | 4.5339 | - | - |  | - | -
|  |  | Paluuveden lämpötila |  |  | - | - | - | 30 | 30 | - | - |  | - | -
|  |  | Virtaama |  |  | - | - | - | -0.00906 | -0.005347 | - | - |  | - | -
|  |  | Painehäviö patt |  |  | - | - | - | #NUM! | #NUM! | - | - |  | - | -
|  |  | Painehäviö vent |  |  | - | - | - | 0.10638 | 0.037054 | - | - |  | - | -
|  |  | Virtausnopeus |  |  | - | - | - | -0.073827 | -0.043572 | - | - |  | - | -
[5 empty] | Virhe |  |  |  | TRUE | TRUE |  |  |  | TRUE
Tarvittava teho
570
-
Tekstejä patterimitoitusosioon
Value out of range. Check parameters.
Not available for selected model

## Puhallinkäyräpisteet (hidden)
[16 empty] | Valinta | 7
1 | Model 60 | [6 empty] | 1 | Model 60
Tulo | Model 60 | [6 empty] | Poisto | Model 60 | [6 empty] | Tulo | Model 53mini | [6 empty] | Poisto | Model 53mini
10 V |  | 7,5 V |  | 5 V |  | 3 V |  | 10 V |  | 7,5 V |  | 5 V |  | 3 V |  | 10 V |  | 7 V |  | 6 V |  | 4V |  | 10 V |  | 7 V |  | 6 V |  | 4V
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
25 | 109.7222 | 20 | 96.508 | 12 | 59.0976 | 10 | 24.8561 | 25 | 116.5344 | 24 | 112.687 | 17 | 72.2846 | 10 | 36.1004 | 25 | 95.3803 | 10 | 84.0396 | 10 | 69.5264 | 10 | 40.0158 | 15 | 103.5755 | 10 | 98.8637 | 10 | 81.983 | 10 | 48.7976
120 | 96.0497 | 100 | 83.3324 | 40 | 51.0413 | 20 | 20.1455 | 120 | 106.0429 | 100 | 101.1625 | 40 | 65.0385 | 20 | 30.2289 | 120 | 88.9477 | 40 | 80.2259 | 25 | 67.2972 | 20 | 37.7479 | 120 | 94.8809 | 40 | 94.8637 | 25 | 79.6966 | 20 | 46.4153
190 | 84.9809 | 150 | 74.1711 | 60 | 44.8522 | 30 | 15.2517 | 190 | 97.2291 | 150 | 92.6182 | 60 | 58.1733 | 30 | 23.2117 | 190 | 83.7627 | 60 | 77.5674 | 35 | 65.7582 | 40 | 32.617 | 190 | 88.808 | 60 | 92.0681 | 35 | 78.1228 | 60 | 34.6466
250 | 74.6059 | 200 | 64.0227 | 80 | 38.2116 | 35 | 12.729 | 250 | 88.5776 | 200 | 82.9624 | 80 | 50.6163 | 35 | 18.9831 | 250 | 78.9265 | 80 | 74.8033 | 55 | 62.5355 | 50 | 29.6194 | 250 | 83.4021 | 80 | 89.1541 | 55 | 74.8411 | 80 | 25.6685
320 | 61.0937 | 250 | 52.4767 | 100 | 31.0031 | 40 | 10.1515 | 320 | 76.3666 | 250 | 71.5994 | 100 | 42.1036 | 43 | 10.0866 | 320 | 72.6742 | 100 | 71.9198 | 140 | 45.3908 | 70 | 21.9159 | 320 | 76.8313 | 100 | 86.1052 | 180 | 46.4366 | 82 | 24.4583
390 | 45.3354 | 300 | 38.7213 | 125 | 20.9155 |  |  | 390 | 58.9808 | 300 | 57.0731 | 140 | 19.5749 |  |  | 370 | 67.6569 | 200 | 54.9175 | 175 | 34.6092 |  |  | 370 | 71.942 | 270 | 48.0489 | 200 | 38.257 | 0 | 0
410 | 40.2277 | 315 | 33.9211 |  |  |  |  | 422 | 44.2778 | 340 | 39.2543 |  |  |  |  | 450 | 58.105 | 260 | 40.7241 |  |  |  |  | 460 | 62.6626 | 280 | 43.7182 | 0 | 0 | 0 | 0
2 | Model 100 | [6 empty] | 2 | Model 100
Tulo | Model 100 | [6 empty] | Poisto | Model 100
10 V |  | 6,5 V |  | 5 V |  | 3 V |  | 10 V |  | 6,5 V |  | 5 V |  | 3 V
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
25 | 105.5599 | 20 | 80.7046 | 10 | 54.339 | 10 | 20.411 | 25 | 115.6788 | 20 | 91.9884 | 15 | 63.4949 | 10 | 29.6705
120 | 91.3341 | 50 | 73.8387 | 40 | 44.8078 | 20 | 15.4146 | 120 | 103.494 | 50 | 86.2865 | 40 | 56.9738 | 20 | 22.5789
190 | 79.8615 | 100 | 61.6656 | 60 | 38.0656 | 25 | 12.8146 | 190 | 93.3922 | 100 | 75.9006 | 60 | 51.1452 | 30 | 16.489
250 | 69.1547 | 150 | 48.3562 | 80 | 30.9537 | 30 | 10.1388 | 250 | 83.6475 | 150 | 63.979 | 80 | 44.536 | 35 | 13.7083
320 | 55.3015 | 170 | 42.6336 | 100 | 23.4037 | 34 | 7.939 | 320 | 70.3402 | 170 | 58.5924 | 100 | 36.7108 | 40 | 11.0677
390 | 39.3343 | 190 | 36.634 | 110 | 19.4367 |  |  | 390 | 53.1577 | 190 | 52.7094 | 125 | 23.2979
400 | 36.815 | 220 | 27.0145 |  |  |  |  | 425 | 41.2632 | 245 | 32.0448
3 | Model 150 | [6 empty] | 3 | Model 150
Tulo | Model 150 | [6 empty] | Poisto | Model 150
10 V |  | 6,5 V |  | 5 V |  | 3 V |  | 10 V |  | 6,5 V |  | 5 V |  | 3 V
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
60 | 163.2762 | 40 | 119.6113 | 25 | 85.8715 | 10 | 45.1029 | 100 | 179.1169 | 50 | 131.1425 | 35 | 96.2168 | 15 | 52.3549
120 | 155.0178 | 50 | 117.5442 | 40 | 82.3209 | 20 | 41.7736 | 120 | 174.8986 | 50 | 131.1425 | 40 | 94.7293 | 20 | 50.4926
190 | 145.3723 | 100 | 107.5157 | 60 | 77.6141 | 25 | 40.0439 | 190 | 162.276 | 100 | 119.3542 | 60 | 88.8966 | 25 | 48.58
250 | 137.0955 | 150 | 97.9473 | 80 | 72.9382 | 30 | 38.2659 | 250 | 153.1626 | 150 | 107.9338 | 80 | 83.2391 | 30 | 46.6127
320 | 127.4285 | 170 | 94.2353 | 100 | 68.2925 | 50 | 30.5755 | 320 | 143.7877 | 170 | 103.4612 | 100 | 77.7419 | 55 | 35.749
350 | 123.282 | 190 | 90.5844 | 130 | 61.3793 |  |  | 390 | 135.3707 | 190 | 99.0404 | 138 | 67.694
420 | 113.5983 | 240 | 81.7056 |  |  |  |  | 450 | 128.7304 | 235 | 89.274
4 | Model 250 | [6 empty] | 4 | Model 250
Tulo | Model 250 | [6 empty] | Poisto | Model 250
7,5 V |  | 7,5 V |  | 6 V |  | 4 V |  | 7,5 V |  | 7,5 V |  | 6 V |  | 4 V
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
20 | 276.93 | 20 | 276.93 | 10 | 213.6134 | 10 | 122.8515 | 25 | 296.297 | 25 | 296.297 | 10 | 231.4548 | 10 | 137.7948
50 | 266.4873 | 50 | 266.4873 | 50 | 195.729 | 20 | 114.8725 | 100 | 266.8495 | 100 | 266.8495 | 50 | 211.5621 | 20 | 129.5056
100 | 247.9086 | 100 | 247.9086 | 90 | 175.4582 | 40 | 97.2905 | 200 | 220.1752 | 200 | 220.1752 | 90 | 189.1132 | 40 | 110.9257
150 | 227.4767 | 150 | 227.4767 | 130 | 151.4758 | 60 | 76.5423 | 230 | 203.5669 | 230 | 203.5669 | 130 | 162.7615 | 60 | 88.0985
230 | 188.9877 | 230 | 188.9877 | 170 | 120.4219 | 80 | 49.8423 | 270 | 178.3132 | 270 | 178.3132 | 170 | 129.2695 | 80 | 55.1025
300 | 144.0084 | 300 | 144.0084 | 205 | 73.943 |  |  | 300 | 155.7556 | 300 | 155.7556 | 200 | 92.4087
340 | 105.2654 | 340 | 105.2654 |  |  |  |  | 340 | 115.6328 | 340 | 115.6328
5 | Model 350 | [6 empty] | 5 | Model 350
Tulo | Model 350 | [6 empty] | Poisto | Model 350
10 V |  | 8 V |  | 6 V |  | 4 V |  | 10 V |  | 8 V |  | 6 V |  | 4 V
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
25 | 368.0233 | 20 | 299.783 | 10 | 213.6134 | 10 | 122.8515 | 25 | 387.0243 | 20 | 322.8487 | 10 | 231.4548 | 10 | 137.7948
100 | 348.743 | 50 | 289.9756 | 50 | 195.729 | 20 | 114.8725 | 100 | 368.0647 | 50 | 312.4056 | 50 | 211.5621 | 20 | 129.5056
200 | 320.9076 | 100 | 272.7309 | 90 | 175.4582 | 40 | 97.2905 | 200 | 340.5875 | 100 | 294.0433 | 90 | 189.1132 | 40 | 110.9257
300 | 289.86 | 150 | 254.131 | 130 | 151.4758 | 60 | 76.5423 | 300 | 309.742 | 150 | 274.2379 | 130 | 162.7615 | 60 | 88.0985
400 | 254.1377 | 230 | 220.5245 | 170 | 120.4219 | 80 | 49.8423 | 400 | 273.8652 | 170 | 265.827 | 170 | 129.2695 | 80 | 55.1025
500 | 210.6472 | 320 | 173.2505 | 205 | 73.943 |  |  | 500 | 229.1915 | 190 | 257.0886 | 200 | 92.4087
610 | 141.3511 | 395 | 114.6459 |  |  |  |  | 580 | 178.9257 | 380 | 141.356
6 | Model 130 | [6 empty] | 6 | Model 130
Tulo | Model 130 | [6 empty] | Poisto | Model 130
10 V |  | 8 V |  | 6 V |  | 4 V |  | 10 V |  | 8 V |  | 6 V |  | 4 V
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
25 | 131.6515 | 20 | 116.8545 | 10 | 86.0149 | 10 | 49.4817 | 25 | 149.372 | 20 | 133.1733 | 15 | 99.9991 | 10 | 61.5554
120 | 122.5295 | 50 | 112.3072 | 40 | 78.9504 | 20 | 45.3946 | 120 | 140.4402 | 50 | 128.5089 | 40 | 94.1082 | 20 | 57.8223
190 | 115.0427 | 100 | 104.2194 | 60 | 73.9658 | 25 | 43.2863 | 190 | 133.1231 | 100 | 120.2105 | 60 | 89.0698 | 30 | 53.8306
250 | 107.9109 | 150 | 95.3292 | 80 | 68.7211 | 30 | 41.1311 | 250 | 126.1684 | 150 | 111.0847 | 80 | 83.6755 | 35 | 51.7192
320 | 98.3807 | 170 | 91.4873 | 100 | 63.171 | 70 | 21.6983 | 320 | 116.9093 | 170 | 107.1393 | 100 | 77.8371 | 80 | 25.8479
390 | 86.684 | 190 | 87.4442 | 180 | 36.2552 |  |  | 390 | 105.6345 | 190 | 102.9859 | 185 | 42.1809
460 | 69.8377 | 320 | 51.7322 |  |  |  |  | 460 | 89.8163 | 325 | 64.0021
7 | Model 53mini | [6 empty] | 7 | Model 53mini
Tulo | Model 53mini | [6 empty] | Poisto | Model 53mini
10 V |  | 7 V |  | 6 V |  | 4V |  | 10 V |  | 7 V |  | 6 V |  | 4V
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
25 | 95.3803 | 10 | 84.0396 | 10 | 69.5264 | 10 | 40.0158 | 15 | 103.5755 | 10 | 98.8637 | 10 | 81.983 | 10 | 48.7976
120 | 88.9477 | 40 | 80.2259 | 25 | 67.2972 | 20 | 37.7479 | 120 | 94.8809 | 40 | 94.8637 | 25 | 79.6966 | 20 | 46.4153
190 | 83.7627 | 60 | 77.5674 | 35 | 65.7582 | 40 | 32.617 | 190 | 88.808 | 60 | 92.0681 | 35 | 78.1228 | 60 | 34.6466
250 | 78.9265 | 80 | 74.8033 | 55 | 62.5355 | 50 | 29.6194 | 250 | 83.4021 | 80 | 89.1541 | 55 | 74.8411 | 80 | 25.6685
320 | 72.6742 | 100 | 71.9198 | 140 | 45.3908 | 70 | 21.9159 | 320 | 76.8313 | 100 | 86.1052 | 180 | 46.4366 | 82 | 24.4583
370 | 67.6569 | 200 | 54.9175 | 175 | 34.6092 |  |  | 370 | 71.942 | 270 | 48.0489 | 200 | 38.257
450 | 58.105 | 260 | 40.7241 |  |  |  |  | 460 | 62.6626 | 280 | 43.7182
8 | Varaus seuraavalle koneelle | [6 empty] | 8 | Varaus seuraavalle koneelle
Tulo | Varaus seuraavalle koneelle | [6 empty] | Poisto | Varaus seuraavalle koneelle
Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s

## C-selection
SELECTED MODEL AND CODE KEY:
Airfi: Device code selection for C-series units | [20 empty] | Airfi Model C5 Water
Select an option from each dropdown menu below | [20 empty] | Code: | #VALUE!
Content description:
Project: | [20 empty] | A | 2 = C = Commercial AHU, Counter-Flow Heat Exchanger
Name: | [20 empty] | BBB | 005, 500dm³/s…1800m³/h (Device: Airfi Model C5 Electric, 230VAC 50Hz 16A, max input power 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max input power 2 kW )
| Airfi Model C5 Water | [19 empty] | C | 2 = L = left (Exhaus air on the left side when viewed from the service side)
[21 empty] | D | 2 = Terminal block version, with actuators wired to the terminal block. Includes, for example, 5 temperature sensors (NTC) and, in the water model, additionally 1 frost protection sensor (NTC). Also includes transmitters according to the selection of the code key. Delivery does not include control regulators.
Code Key: | Basic structure: |  |  |  | Filters: |  | Coils: |  |  |  | Accessories: | [5 empty] | Controls: |  |  |  | E | 7 = ISO ePM1 85% (F8/F9 level)
| A | BBB | C | D | E | F | GG | H | I | J | K | L | M | N | O | P | Q | RR | S |  | F | 5 = ISO ePM10 50%, (Standard delivery in C series unless otherwise specified) (Previous classification: M5 level)
Selection: | 2 | 005 | 2 | #VALUE! | 7 | 5 | 61 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 00 | 9 |  | GG | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified.
[21 empty] | H | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified.
BASIC STRUCTURE: | [20 empty] | I | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified.
(A) Unit type | [20 empty] | J | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified.
[21 empty] | K | 0 = No filter monitors. Standard delivery unless otherwise specified.
(BBB) Unit size | [20 empty] | L | 0 = No constant pressure regulators. Standard delivery unless otherwise specified.
[21 empty] | M | 0 = No air volume flow measurement. Standard delivery unless otherwise specified.
(C) Unit orientation – Note! Ensure the ductwork configuration | [20 empty] | N | 0 = No dampers or actuators for exhaust and outdoor air. Standard delivery unless otherwise specified.
[21 empty] | O | 0 = No sensors. Standard delivery unless otherwise specified.
(D) Unit automation | [20 empty] | P | 0 = No energy meters. Standard delivery unless otherwise specified.
[21 empty] | Q | 0 = No controller. Standard delivery for terminal block units; no other option available.
FILTERS: | [20 empty] | RR | 00 = Default (not selected). Standard delivery unless otherwise specified.
(E) Supply air filtration | [20 empty] | S | 9 = Delivery according to the specification list
(F) Exhaust air filtration
COILS:
(GG) Internal post-heating
(H) Internal post-heating control
(I) Internal cooling
(J) Internal cooling control (cooling coil)
ACCESSORIES:
(K) Filter monitor*
(L) Constant pressure regulator*
(M) Air volume flow measurement*
(N) Spring-return dampers
(O) Internal measurement sensors*
(P) Energy meter**
CONTROLS:
(Q) Control 1 – delivered separately, installed on-site
(RR) Control 2 – delivered separately, installed on-site
(S) Additional information
Version 7.3
FI
ENG

## C-series
[12 empty] | Version 7.3 | [11 empty] | Version 7.3 | SELECTED MODEL AND CODE KEY:
Airfi: C series air handling unit selection program | [12 empty] | Calculation of annual efficiency for exhaust air heat recovery | [11 empty] | Airfi Model C5 Water
Project: | [24 empty] | Code: | #VALUE!
Name: | [9 empty] | 1 | [14 empty] | Content description:
[13 empty] | Project: | [11 empty] | A | 2 = C = Commercial AHU, Counter-Flow Heat Exchanger
Selected model: | [12 empty] | Name: |  |  |  |  | = insert value | [6 empty] | BBB | 005, 500dm³/s…1800m³/h (Device: Airfi Model C5 Electric, 230VAC 50Hz 16A, max input power 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max input power 2 kW )
Airfi Model C5 Water |  | Code: | #VALUE! | [21 empty] | C | 2 = L = left (Exhaus air on the left side when viewed from the service side)
[13 empty] | Calculation parameters: |  |  |  | Outdoor air temperature [°C] | Percentage of the year | Exhaust air temperature | Supply air temperature | SS,Kd | ST,Kd | SJ,Kd |  | D | 2 = Terminal block version, with actuators wired to the terminal block. Includes, for example, 5 temperature sensors (NTC) and, in the water model, additionally 1 frost protection sensor (NTC). Also includes transmitters according to the selection of the code key. Delivery does not include control regulators.
[25 empty] | E | 7 = ISO ePM1 85% (F8/F9 level)
[13 empty] | Supply air volume flow, through heat recovery | qtLTO | 125 | dm3/s | -32 | 0% | -6.5 | -4.5 | 0 | 0 | 0 |  | F | 5 = ISO ePM10 50%, (Standard delivery in C series unless otherwise specified) (Previous classification: M5 level)
[13 empty] | Extract air volume flow, through heat recovery | qpLTO | 125 | dm3/s | -31 | 0% | -6.5 | -3.5 | 0 | 0 | 0 |  | GG | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified.
[13 empty] | Supply air to extract air ratio for volume flow through heat recovery |  |  |  | -30 | 0% | -6.5 | -2.5 | 0 | 0 | 0 |  | H | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified.
[14 empty] | RLTO | 1 |  | -29 | 0% | -6.5 | -1.5 | 0 | 0 | 0 |  | I | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified.
[17 empty] | -28 | 0% | -6.5 | -0.5 | 0 | 0 | 0 |  | J | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified.
[13 empty] | Additional extract air flow rate included in heat recovery requirements |  |  |  | -27 | 0% | -6.5 | 0.5 | 0 | 0 | 0 |  | K | 0 = No filter monitors. Standard delivery unless otherwise specified.
[14 empty] | qep1 | 0 | dm3/s | -26 | 0% | -6.5 | 1.5 | 0 | 0 | 0 |  | L | 0 = No constant pressure regulators. Standard delivery unless otherwise specified.
[13 empty] | Operational time of the additional extract air | Tqep1 | 0 | h / day | -25 | 0% | -6.5 | 2.5 | 0 | 0 | 0 |  | M | 0 = No air volume flow measurement. Standard delivery unless otherwise specified.
[13 empty] | Supply / extract air volume flow ratio for entire ventilation system |  |  |  | -24 | 0% | -6.5 | 3.5 | 0 | 0 | 0 |  | N | 0 = No dampers or actuators for exhaust and outdoor air. Standard delivery unless otherwise specified.
[14 empty] | RT | 1 |  | -23 | 0% | -6.5 | 4.5 | 0 | 0 | 0 |  | O | 0 = No sensors. Standard delivery unless otherwise specified.
[17 empty] | -22 | 0% | -6.5 | 5.5 | 0 | 0 | 0 |  | P | 0 = No energy meters. Standard delivery unless otherwise specified.
[13 empty] | Heat recovery cell efficiency (EN 308) | η | 86.98% |  | -21 | 0% | -6.5 | 6.5 | 0 | 0 | 0 |  | Q | 0 = No controller. Standard delivery for terminal block units; no other option available.
[13 empty] | Supply side temperature ratio for balanced air flow (EN 13141-7) | ηt(RLTO=1) | 83.1% |  | -20 | 0% | -6.5 | 7.5 | 0 | 0 | 0 |  | RR | 00 = Default (not selected). Standard delivery unless otherwise specified.
[13 empty] | Supply side temperature ratio | ηt(RLTO) | 83.1% |  | -19 | 0% | -6.5 | 8.5 | 0 | 0 | 0 |  | S | 9 = Delivery according to the specification list
[17 empty] | -18 | 0% | -6.5 | 9.5 | 0 | 0 | 0
[13 empty] | Select climate zone (city) |  |  |  | -17 | 0% | -6.5 | 10.5 | 0 | 0 | 0
[13 empty] | Indoor temperature | ts | 21 | °C | -16 | 0% | -6.5 | 11.5 | 0 | 0 | 0
[13 empty] | Minimum exhaust air temperature | tj,min | -6.5 | °C | -15 | 0% | -6.5 | 12.5 | 0 | 0 | 0
[13 empty] | Supply air temperature limitation |  |  |  | -14 | 0% | -6.5 | 13.5 | 0 | 0 | 0
[13 empty] | Maximum supply air temperature in a limited situation | tt,max | 20 | °C | -13 | 0% | -6.5 | 14.5 | 0 | 0 | 0
[17 empty] | -12 | 0.03425% | -6.423 | 15.423 | 4.125 | 3.4279 | 3.4279
[13 empty] | Annual efficiency | ηₐ | 83.1% |  | -11 | 0.137% | -5.592 | 15.592 | 12 | 9.972 | 9.972
|  | 125 |  | 125 | [12 empty] | -10 | 0.4909% | -4.761 | 15.761 | 40.0417 | 33.2746 | 33.2746
[13 empty] | Total energy demand for ventilation |  | 15973.9722 | kWh/a | -9 | 0.6735% | -3.93 | 15.93 | 20 | 16.62 | 16.62
[13 empty] | Recovered heating energy |  | 13274.3709 | kWh/a | -8 | 0.9132% | -3.099 | 16.099 | 25.375 | 21.0866 | 21.0866
[13 empty] | Electricity consumption of fans and electronics |  | 1123.2064 | kWh/a | -7 | 1.13% | -2.268 | 16.268 | 22.1667 | 18.4205 | 18.4205
[17 empty] | -6 | 2.386% | -1.437 | 16.437 | 123.75 | 102.8362 | 102.8362
[17 empty] | -5 | 4.292% | -0.606 | 16.606 | 180.9167 | 150.3417 | 150.3417
[17 empty] | -4 | 5.685% | 0.225 | 16.775 | 127.0833 | 105.6063 | 105.6063
Operating point (insert air flow and pressure difference values): | [6 empty] | Boost situation calculation: | [9 empty] | -3 | 8.094% | 1.056 | 16.944 | 211 | 175.341 | 175.341
|  | Supply air |  | Extract air |  |  | Maximum boost reserve: |  | Supply air | Extract air | [6 empty] | -2 | 11.11% | 1.887 | 17.113 | 253 | 210.243 | 210.243
Air volume flow: |  | 450 | m³/h | 450 | m³/h |  |  |  | 153.8% | 158.3% | [6 empty] | -1 | 15.72% | 2.718 | 17.282 | 370.3333 | 307.747 | 307.747
|  | 125 | dm³/s | 125 | dm³/s | [11 empty] | 0 | 21.26% | 3.549 | 17.451 | 424.375 | 352.6556 | 352.6556
Pressure difference: |  | 125 | Pa | 125 | Pa |  | Insert the desired boost value: | [9 empty] | 1 | 24.16% | 4.38 | 17.62 | 211.6667 | 175.895 | 175.895
[7 empty] | Boost value [%]: |  |  | 5% | [6 empty] | 2 | 30.03% | 5.211 | 17.789 | 407.7083 | 338.8056 | 338.8056
|  | Supply fan: |  | Extract fan: | [12 empty] | 3 | 34.85% | 6.042 | 17.958 | 316.5 | 263.0115 | 263.0115
Control voltage: |  | 4.1064 | V | 3.8308 | V |  | Operating point in boost situation: | [9 empty] | 4 | 40.25% | 6.873 | 18.127 | 335.0417 | 278.4196 | 278.4196
Fan power: |  | 65.645 | W | 58.1749 | W |  |  |  | Supply air | Extract air | [6 empty] | 5 | 44.12% | 7.704 | 18.296 | 226 | 187.806 | 187.806
[7 empty] | Air volume flow: |  | 472.5 | 472.5 | m³/h | [5 empty] | 6 | 46.19% | 8.535 | 18.465 | 113.125 | 94.0069 | 94.0069
Total power: | 128.2199 | W | [6 empty] | 131.25 | 131.25 | dm³/s | [5 empty] | 7 | 50.45% | 9.366 | 18.634 | 217.5833 | 180.8118 | 180.8118
SFP: | 1.0258 | kW/(m³/s) | SFPint : | 303.7953 | W/(m³/s) |  | Pressure difference: |  | 137.8125 | 137.8125 | Pa | [5 empty] | 8 | 54.59% | 10.197 | 18.803 | 196.625 | 163.3954 | 163.3954
SPI: | 0.28493 | W/(m³/h) | SFPint_limit : | 1241 | W/(m³/s) |  | Control voltage: |  | 4.2808 | 4.0011 | V | [5 empty] | 9 | 58.04% | 11.028 | 18.972 | 151 | 125.481 | 125.481
Note: The above values also include the device's electronics. | [16 empty] | 10 | 62.18% | 11.859 | 19.141 | 166.375 | 138.2576 | 138.2576
[17 empty] | 11 | 64.63% | 12.69 | 19.31 | 89.5833 | 74.4438 | 74.4438
Sound power levels in connection ducts | [16 empty] | 12 | 69.67% | 13.521 | 19.479 | 165.375 | 137.4266 | 137.4266
Connection duct | Sound power levels in octave bands LW,oct [dB] | [8 empty] | LWtot [dB] | LWAtot [dB] | [8 empty] | Total | 4410.75 | 3665.3332 | 3665.3332
| 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz |  | 4 kHz | 8 kHz
Supply air | 67.6283 | 67.6283 | 60.6283 | 54.6283 | 54.6283 | 50.6283 |  | 42.6283 | 35.6283 | 71.2898 | 59.6283 | [5 empty] | SI,Kd = heating degree days, between indoor air and outdoor air, Kd
Outdoor air | 56.7359 | 58.7359 | 46.7359 | 41.7359 | 34.7359 | 25.7359 |  | 22.7359 | 21.7359 | 61.0885 | 45.7359
Extract air | 55.1053 | 58.1053 | 50.1053 | 43.1053 | 39.1053 | 31.1053 |  | 24.1053 | 24.1053 | 60.4269 | 47.0702 | [5 empty] | SS,Kd = heating degree days, between supply air and outdoor air, Kd
Exhaust air | 64.2251 | 64.2251 | 59.2251 | 54.2251 | 53.2251 | 50.2251 |  | 41.2251 | 36.2251 | 68.2769 | 58.3398
SE,Kd = heating degree days, between exhaust air and outdoor air, Kd
Sound power levels through casing:
| Sound power levels in octave bands LW,oct [dB] | [8 empty] | LWtot [dB] | LWAtot [dB]
| 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz |  | 4 kHz | 8 kHz
Through casing | 55.7211 | 54.7211 | 49.7211 | 36.7211 | 33.7211 | 32.7211 |  | 23.7211 | 22.7211 | 58.882 | 44.5689
Sound pressure level in a room with an absorption area of 10m²: | [9 empty] | LpA,10m²Sab [dB] | 40.5895
All rights reserved. |  | www.airfi.fi | www.airfi.eu | [9 empty] | All rights reserved. | www.airfi.fi | www.airfi.eu
Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program. | [12 empty] | Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program.
The selection program is made by Zenner Engineers. The program is based on laboratory measurements according to SFS-EN 13141-7. | [12 empty] | The selection program is made by Zenner Engineers. The program is based on laboratory measurements according to SFS-EN 13141-7.
DIMENSIONING OF WATER-BASED HEATING AND COOLING COILS |  |  |  |  | Note: Coil dimensioning is successful when there are no error messages in the calculation. Adjust the inlet or outlet water temperatures if necessary.
Dimensioning of water-based heating coil
The selected coil model is suitable for heating water ~50/30
Insert parameters:
Start by inserting either inlet or outlet water temperature
Inlet air temperature |  |  | -5 | ºC | Heating coil dimensioning by inlet water temperature
Outlet air temperature |  |  | 20 | ºC | Inlet water temperature |  |  |  |  | 50 | ºC
Inlet water temperature |  |  | 50 | ºC | Outlet water temperature |  |  |  |  | 30.9637 | ºC
Outlet water temperature |  |  | 30 | ºC | Volume flow |  |  |  |  | 0.049771 | dm³/s
[5 empty] | Heating coil fluid side pressure loss |  |  |  |  | 0.45463 | kPa
Supply air volume flow |  |  | 125 | dm3/s | Control valve pressure loss (Airfi implementation)* |  |  |  |  | - | kPa
Required heating power |  |  | 3.9661 | kW | Flow rate in the coil's pipe circuit |  |  |  |  | 0.16366 | m/s
Heating coil dimensioning by outlet water temperature
[5 empty] | Inlet water temperature |  |  |  |  | - | ºC
[5 empty] | Outlet water temperature |  |  |  |  | - | ºC
[5 empty] | Volume flow |  |  |  |  | - | dm³/s
[5 empty] | Heating coil fluid side pressure loss |  |  |  |  | - | kPa
* No control valve or actuator / heating group selected. |  |  |  |  | Control valve pressure loss (Airfi implementation)* |  |  |  |  | - | kPa
[5 empty] | Flow rate in the coil's pipe circuit |  |  |  |  | - | m/s
Value out of range. Check input parameters.
Dimensioning of water-based cooling coil |  |  |  |  | Note: Coil dimensioning is successful when there are no error messages in the calculation. Adjust the inlet or outlet water temperatures if necessary.
The selected coil model is suitable for cooling water ~7/12
Insert parameters:
Start by inserting either inlet or outlet water temperature
Inlet air temperature |  |  | 25 | ºC | Cooling coil dimensioning by inlet water temperature
Inlet air relative humidity |  |  | 65 | %RH | Inlet water temperature |  |  |  |  | - | ºC
Outlet air temperature |  |  | 17 | ºC | Outlet water temperature |  |  |  |  | - | ºC
Inlet water temperature |  |  | 7 | ºC | Volume flow |  |  |  |  | - | dm³/s
Outlet water temperature |  |  | 12 | ºC | Patterin nestepuolen painehäviö |  |  |  |  | - | kPa
[5 empty] | Control valve pressure loss (Airfi implementation)* |  |  |  |  | - | kPa
Supply air volume flow |  |  | 125 | dm³/s | Flow rate in the coil's pipe circuit |  |  |  |  | - | m/s
Required cooling capacity (sensible) |  |  | 1.212 | kW | Value out of range. Check input parameters.
Required total cooling capacity |  |  | 1.7876 | kW | Cooling coil dimensioning by outlet water temperature
[5 empty] | Inlet water temperature |  |  |  |  | - | ºC
[5 empty] | Outlet water temperature |  |  |  |  | - | ºC
[5 empty] | Volume flow |  |  |  |  | - | dm³/s
[5 empty] | Patterin nestepuolen painehäviö |  |  |  |  | - | kPa
* No control valve or actuator / cooling group selected. |  |  |  |  | Control valve pressure loss (Airfi implementation)* |  |  |  |  | - | kPa
[5 empty] | Flow rate in the coil's pipe circuit |  |  |  |  | - | m/s
Value out of range. Check input parameters.
Version 7.3
FI
ENG
Supply air
Extract air

## C5 validointi (hidden)
| Tulokanava |  |  | Vohj | W | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LWAtot
| 390.5 | l/s | Mitattu | 8 | 477 | 72.6 | 69.2 | 78.8 | 71.3 | 67.2 | 66.5 | 60.2 | 61.1 | 81.1 | 74.3
| 405.9 | Pa | Laskuri | 8 | 485 | 74.511 | 70.511 | 78.511 | 70.511 | 67.511 | 66.511 | 60.511 | 60.511 | 81.274 | 74.511
|  |  | Ero | 0% | -1.649% | 1.911 | 1.311 | -0.28899 | -0.78899 | 0.31101 | 0.011011 | 0.31101 | -0.58899 | 0.17405 | 0.21101
Airfi C5-koneen laskentaohjelman validointipisteitä
Laskentaohjelmaversio 7.0 beta
24.10.2024 / JK
| Ulkokanava |  |  | Vohj | W | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LWAtot
| 277.6 | l/s | Mitattu | 6 | 207.8 | 59.8 | 58.3 | 49.7 | 46.9 | 39.2 | 33.3 | 28 | 22.2 | 62.5 | 47.9
| 219.7 | Pa | Laskuri | 5.9863 | 203 | 60.6012 | 58.6012 | 52.6012 | 48.6012 | 40.6012 | 35.6012 | 29.6012 | 26.6012 | 63.3124 | 49.6012
|  |  | Ero | 0.2283% | 2.365% | 0.80119 | 0.30119 | 2.9012 | 1.7012 | 1.4012 | 2.3012 | 1.6012 | 4.4012 | 0.8124 | 1.7012
| Poistokanava |  |  | Vohj | W | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LWAtot
| 490 | l/s | Mitattu | 10 | 725.6 | 68.9 | 61 | 64.3 | 57.3 | 53.3 | 50 | 46 | 41.2 | 71 | 60.1
| 500 | Pa | Laskuri | 9.9073 | 710.026 | 68.6536 | 62.6536 | 64.6536 | 57.6536 | 53.6536 | 49.6536 | 45.6536 | 38.6536 | 71.1553 | 60.6083
|  |  | Ero | 0.936% | 2.193% | -0.24636 | 1.6536 | 0.35364 | 0.35364 | 0.35364 | -0.34636 | -0.34636 | -2.5464 | 0.15528 | 0.50827
| Jätekanava |  |  | Vohj | W | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LWAtot
| 239.4 | l/s | Mitattu | 4 | 74.8 | 60.8 | 61.8 | 57.6 | 53.2 | 53.2 | 49.4 | 41 | 35.4 | 65.8 | 57.4
| 58.5 | Pa | Laskuri | 4.0629 | 75.4327 | 64.3558 | 64.3558 | 59.3558 | 54.3558 | 53.3558 | 50.3558 | 41.3558 | 36.3558 | 68.4077 | 58.4706
|  |  | Ero | -1.548% | -0.8387% | 3.5558 | 2.5558 | 1.7558 | 1.1558 | 0.15583 | 0.95583 | 0.35583 | 0.95583 | 2.6077 | 1.0706
| Vaipan läpi |  |  | Vohj | W | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LWAtot
Tulo | 386.1 | l/s | Mitattu | 8 | 1000.8 | 60.1 | 57.8 | 53.8 | 40.7 | 39.9 | 39 | 31.6 | 29.9 | 62.8 | 48.6
| 405.9 | Pa | Laskuri | 7.9919 | 994.9326 | 60.3998 | 59.3998 | 54.3998 | 41.3998 | 38.3998 | 37.3998 | 28.3998 | 27.3998 | 63.5607 | 49.2476
Poisto | 417.6 | l/s | Ero | 0.1012% | 0.5897% | 0.29982 | 1.5998 | 0.59982 | 0.69982 | -1.5002 | -1.6002 | -3.2002 | -2.5002 | 0.7607 | 0.64757
| 422.6 | Pa

## TuloksetC (hidden)
[53 empty] | dB-ruksittu |  | FALSE | dB Package | [39 empty] | Tuloilman rajoituksen ehdot kielivalinnasta riippuen (v.5.8 ja 5.9)
[28 empty] | KIELIVALINTA | [24 empty] | Model 60 tai 100 |  | TRUE |  | Ei valintamahdollisuutta Model 150:lle, v4.4 (18.11.2019), eikä model 250 ja 350 | [38 empty] | Kielivalinta |  |  |  | 1
[22 empty] | Liukuvalinta | [5 empty] | Kielivalinta ja sen vaikutus syöttösoluihin | [5 empty] | Kielen valinnan vaikutus käyrien tulostukseen (dm³/s vai m³/h) | [18 empty] | Valinta |  | FALSE | [40 empty] | FALSE | Suomi |  |  | 21
[22 empty] | 1 | [5 empty] | 2 | Valittu kieli |  |  |  |  | Yläakseli: |  | Air volume flow [dm³/s] | [59 empty] | TRUE | Muut kielet
|  | 1 | Valinta, huom. Numerot muutettu siten että koneet suuruusjärjestyksessä | [18 empty] | Muutettu laskentaohjelman järjestysnumeroksi | [11 empty] | Ala-akseli: |  | Air volume flow [m³/h] | [18 empty] | dB Package vaimennus
[22 empty] | 1 | [5 empty] | FALSE | Suomi | [25 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
|  | Ilmamääräkäyrät | [25 empty] | TRUE | Muut kielet |  |  |  |  | Ilmamääräkäyrät | [19 empty] | Vaimennus | 8 | 3 | 5 | 4 | 3 | 3 | 5 | 3 | [26 empty] | Tehostuksen piirto |  |  |  | Kielivalinnan vaikutus |  |  | Kielivalinta tuloilman lämpötilarajoitukseen
|  | Tulo | [10 empty] | Poisto | [8 empty] | Muokattu koneet suuruusjärjestykseen | [11 empty] | Tulo | [8 empty] | Poisto | [9 empty] | a-painotus | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | [22 empty] | Tehostusvara |  |  |  |  | Tuloilma | l/s | Pa |  | Tuloilma | l/s | Pa | Suomi | Muut |  | Valinta | Lukema
|  | 10 V |  | 8 V |  | 6 V |  | 4 V |  |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V | [8 empty] | m³/h | [5 empty] | 10 V |  | 8 V |  | 6 V |  | 4 V |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V | [34 empty] | Haluttu tehostus |  |  |  |  | Origo | 1 | 0.008 |  | Origo | 3.6 | 0.008 | 17 | 21 |  | 21 | 21
| 10V dm³/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  |  | 10V dm³/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  | Liukuvalinta |  | Laskentaohjelma |  |  |  | dm³/s | [5 empty] | Pa | m³/h | Pa | m³/h | Pa | m³/h | Pa | m³/h |  | Pa | m³/h | Pa | m³/h | Pa | m³/h | Pa | m³/h | [33 empty] | 5% |  |  |  |  | Mitoitus | 125 | 125 |  | Mitoitus | 450 | 125 | 18 | 22 |  | 22 | 22
| 615.8098 | 25 | 615.8098 | 20 | 541.1654 | 10 | 383.0095 | 10 | 227.8208 |  |  | 704.4152 | 25 | 704.4152 | 20 | 635.1311 | 10 | 461.4662 | 10 | 281.0751 |  | 1 | C5 | 1 | [9 empty] | 25 | 2216.9155 | 20 | 1948.1955 | 10 | 1378.8343 | 10 | 820.155 |  | 25 | 2535.8945 | 20 | 2286.4719 | 10 | 1661.2783 | 10 | 1011.8703 |  |  |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | LpA10m2 | LpA2,5m2 | [23 empty] | Tehostus | 131.25 | 137.8125 |  | Tehostus | 472.5 | 137.8125 | 19 | 23 |  | 23 | 23
| 591.8867 | 100 | 591.8867 | 50 | 528.9495 | 50 | 360.8293 | 20 | 219.2911 |  |  | 672.6394 | 100 | 672.6394 | 50 | 621.1372 | 50 | 436.2265 | 20 | 271.669 |  | 2 | ** C series future version ** | 1 |  |  |  | Mitoituspisteen tilavuusvirrat dm³/s | [5 empty] | 100 | 2130.7922 | 50 | 1904.2183 | 50 | 1298.9853 | 20 | 789.448 |  | 100 | 2421.5017 | 50 | 2236.094 | 50 | 1570.4155 | 20 | 978.0086 |  |  | C5 | 47.7211 | 51.7211 | 44.7211 | 32.7211 | 30.7211 | 29.7211 | 18.7211 | 19.7211 | 53.8313 | 40.555 | 36.5756 | 42.5962 | [18 empty] | Halutun tehostuksen toimintapiste: |  |  |  |  | Poistoilma | l/s | Pa |  | Poistoilma | l/s | Pa | 20 | 24 |  | 24 | 24
| 558.8493 | 200 | 558.8493 | 100 | 508.0684 | 90 | 337.5265 | 40 | 201.6434 |  |  | 629.3306 | 200 | 629.3306 | 100 | 597.2455 | 90 | 409.7502 | 40 | 252.0807 |  | 3 | ** C series future version ** | 1 |  |  |  | Tulo | Poisto |  |  |  |  | 200 | 2011.8577 | 100 | 1829.0462 | 90 | 1215.0954 | 40 | 725.9161 |  | 200 | 2265.5903 | 100 | 2150.0837 | 90 | 1475.1007 | 40 | 907.4906 |  |  | ** C series future version ** | -8 | -3 | -5 | -4 | -3 | -3 | -5 | -3 | 5.0431 | 3.4162 | -0.56325 | 5.4574 |  |  |  |  | Keittiöohitus valinta |  |  | Tekstit | [10 empty] | (Toisen potenssin verkkokäyrästä suoraan): |  |  |  |  | Origo | 2 | 0.032 |  | Origo | 7.2 | 0.032 | 21 | 25 |  | 25 | 25
| 524.3502 | 300 | 524.3502 | 150 | 486.4778 | 130 | 312.9113 | 60 | 183.1124 |  |  | 584.8675 | 300 | 584.8675 | 150 | 572.5831 | 130 | 381.8354 | 60 | 231.2983 |  | 4 | ** C series future version ** | 1 |  |  |  | 125 | 125 |  |  |  |  | 300 | 1887.6607 | 150 | 1751.32 | 130 | 1126.4808 | 60 | 659.2047 |  | 300 | 2105.523 | 150 | 2061.2991 | 130 | 1374.6073 | 60 | 832.6739 |  |  | ** C series future version ** | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0309 | 6.9871 | 3.0077 | 9.0283 | Poistettu Model 150 dB-paketti mahdollisuus18.11.2019 |  |  |  | FALSE |  |  | Kitchen bypass* |  | * With kitchen bypass, the total extract air volume flow is larger than the inserted value | [8 empty] | Tulo | Poisto |  |  |  | Mitoitus | 125 | 125 |  | Mitoitus | 450 | 125
| 488.1761 | 400 | 488.1761 | 230 | 450.2577 | 170 | 286.7334 | 160 | 69.7881 |  |  | 539.1524 | 400 | 539.1524 | 170 | 562.485 | 170 | 352.2185 | 160 | 95.1047 |  | 5 | ** C series future version ** | 1 | [9 empty] | 400 | 1757.434 | 230 | 1620.9279 | 170 | 1032.2401 | 160 | 251.2372 |  | 400 | 1940.9487 | 170 | 2024.9459 | 170 | 1267.9865 | 160 | 342.3768 |  |  | Model 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ei Model 250:ssä | [6 empty] | Kitchen bypass |  | * Not available for the selected model | [8 empty] | 131.25 | 131.25 | l/s |  |  | Tehostus | 131.25 | 137.8125 |  | Tehostus | 472.5 | 137.8125
| 450.0566 | 500 | 450.0566 | 320 | 406.5835 | 320 | 166.5933 |  |  |  |  | 492.0732 | 500 | 492.0732 | 190 | 552.2452 | 330 | 206.7626 |  |  |  | 6 | ** C series future version ** | 1 | [9 empty] | 500 | 1620.2037 | 320 | 1463.7007 | 320 | 599.736 |  |  |  | 500 | 1771.4636 | 190 | 1988.0828 | 330 | 744.3454 |  |  |  |  | Model 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ei Model 350:ssä | [5 empty] | Valinta | Kitchen bypass | [10 empty] | 137.8125 | 137.8125 | Pa | [15 empty] | Vesimalli
| 442.17 | 520 | 442.17 | 510 | 299.9803 | [6 empty] | 477.6646 | 530 | 477.6646 | 510 | 362.1499 | [17 empty] | 520 | 1591.8121 | 510 | 1079.9292 | [5 empty] | 530 | 1719.5925 | 510 | 1303.7397 | [6 empty] | Model 130 | -8 | -3 | -5 | -4 | -3 | -3 | -5 | -3 | 5.0431 | 3.4162 | -0.56325 | 5.4574 | [17 empty] | Vesipatteri | [18 empty] | TRUE
[83 empty] | TRUE | 472.5 | 472.5 | m³/h
[15 empty] | Äänet | [54 empty] | Keittiöohitus | [13 empty] | 131.25 | 131.25 | dm³/s |  | Max tehostus |  | Tarkistus |  | Ohjausjännite
|  |  | Tulopuhallin |  |  | Poistopuhallin |  |  | Elektroniikka |  |  |  |  | Kennon | Tulokanava | [9 empty] | Ulkokanava | [9 empty] | Poistokanava | [9 empty] | Jätekanava | [9 empty] | Vaipan läpi | [14 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | SFPint | SFPint_limit | Malli, teksti | Sähkönsyöttö, teksti |  |  |  |  | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto |  |  | LTO-hyötysuhteet v6.0 eteenpäin | [5 empty] | Jälkilämmityspatterin
|  |  | Tarkistus | Ohjaus | Teho | Tarkistus | Ohjaus | Teho | Teho | Total teho | SFP | Vert qV | SFP vert | hyötys | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | LpA10m2 | LpA2,5m2 |  |  | Model 60 | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 54.9195 | 303.7953 | 1241 | #REF! | 230 V, 50 Hz, max 2 kW | C5 |  |  |  | 153.8% | 158.3% | TRUE | TRUE | 4.2808 | 4.0011 | [6 empty] | EN 13141-7 | EN 308 | ottoteho
1 |  | C5 | TRUE | 4.1064 | 65.645 | TRUE | 3.8308 | 58.1749 | 4.4 | 128.2199 | 1.0258 | 385 | 0.99834 | 0.85 | 67.6283 | 67.6283 | 60.6283 | 54.6283 | 54.6283 | 50.6283 | 42.6283 | 35.6283 | 71.2898 | 59.6283 | 56.7359 | 58.7359 | 46.7359 | 41.7359 | 34.7359 | 25.7359 | 22.7359 | 21.7359 | 61.0885 | 45.7359 | 55.1053 | 58.1053 | 50.1053 | 43.1053 | 39.1053 | 31.1053 | 24.1053 | 24.1053 | 60.4269 | 47.0702 | 64.2251 | 64.2251 | 59.2251 | 54.2251 | 53.2251 | 50.2251 | 41.2251 | 36.2251 | 68.2769 | 58.3398 | 55.7211 | 54.7211 | 49.7211 | 36.7211 | 33.7211 | 32.7211 | 23.7211 | 22.7211 | 58.882 | 44.5689 | 40.5895 | 46.6101 |  |  | Model 100 | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 54.9195 | - | - | ** C-series ** |  | ** C series future version ** | [11 empty] | 1 |  | C5 |  | 83.1% | 86.98% | 2000
2 |  | ** C series future version ** | [66 empty] | Model 150 | - | - | - | - | - | - | - | - | - | - | - | - | ** C-series ** |  | ** C series future version ** | [11 empty] | 2 |  | ** C series future version **
3 |  | ** C series future version ** | [66 empty] | Model 250 | - | - | - | - | - | - | - | - | - | - | - | - | ** C-series ** |  | ** C series future version ** | [11 empty] | 3 |  | ** C series future version **
4 |  | ** C series future version ** | [66 empty] | Model 350 | - | - | - | - | - | - | - | - | - | - | - | - | ** C-series ** |  | ** C series future version ** | [11 empty] | 4 |  | ** C series future version **
5 |  | ** C series future version ** | [66 empty] | Model 130 | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 54.9195 | - | - | ** C-series ** |  | ** C series future version ** | [11 empty] | 5 |  | ** C series future version **
6 |  | ** C series future version ** | [93 empty] | 6 |  | ** C series future version **
Huom. Valinta erilainen kuin aiemmat sarakkeet vasemmalla
|  |  | Tulopuhallin |  |  | Poistopuhallin |  |  | Elektroniikka | [5 empty] | Tulokanava | [9 empty] | Ulkokanava | [9 empty] | Poistokanava | [9 empty] | Jätekanava | [9 empty] | Vaipan läpi | [14 empty] | Keittiöohitus | [13 empty] | Tehostuksen toimintapiste |  |  |  | Max tehostus |  | Tarkistus |  | Ohjausjännite |  |  | Tehostus positiivinen luku
|  |  | Tarkistus | Ohjaus | Teho | Tarkistus | Ohjaus | Teho | Teho | Total | SFP | Vert qV | SFP vert | Hyötys. | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | LpA10m2 | LpA2,5m2 | SEC | Class |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwA | SFPint | SFPint_limit |  | Sähkönsyöttö, teksti | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto | Tulo | Poisto | [6 empty] | EN 13141-7 | EN 308
|  | Valinta | TRUE | 4.1064 | 65.645 | TRUE | 3.8308 | 58.1749 | 4.4 | 128.2199 | 1.0258 | 385 | 0.99834 | 0.85 | 67.6283 | 67.6283 | 60.6283 | 54.6283 | 54.6283 | 50.6283 | 42.6283 | 35.6283 | 71.2898 | 59.6283 | 56.7359 | 58.7359 | 46.7359 | 41.7359 | 34.7359 | 25.7359 | 22.7359 | 21.7359 | 61.0885 | 45.7359 | 55.1053 | 58.1053 | 50.1053 | 43.1053 | 39.1053 | 31.1053 | 24.1053 | 24.1053 | 60.4269 | 47.0702 | 64.2251 | 64.2251 | 59.2251 | 54.2251 | 53.2251 | 50.2251 | 41.2251 | 36.2251 | 68.2769 | 58.3398 | 55.7211 | 54.7211 | 49.7211 | 36.7211 | 33.7211 | 32.7211 | 23.7211 | 22.7211 | 58.882 | 44.5689 | 40.5895 | 46.6101 | -70.406 | A+ |  | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 54.9195 | 303.7953 | 1241 | #REF! | 230 V, 50 Hz, max 2 kW | 472.5 | 472.5 | 137.8125 | 137.8125 | 153.8% | 158.3% | TRUE | TRUE | 4.2808 | 4.0011 |  | TRUE | Valinta |  | C5 |  | 0.831 | 0.86975 | 2000
[84 empty] | 131.25 | 131.25
|  | Tulosteeseen |  | 4.1064 | 65.645 |  | 3.8308 | 58.1749 |  | 128.2199 | 1.0258 | 385 | 0.99834 | 0.85 | 67.6283 | 67.6283 | 60.6283 | 54.6283 | 54.6283 | 50.6283 | 42.6283 | 35.6283 | 71.2898 | 59.6283 | 56.7359 | 58.7359 | 46.7359 | 41.7359 | 34.7359 | 25.7359 | 22.7359 | 21.7359 | 61.0885 | 45.7359 | 55.1053 | 58.1053 | 50.1053 | 43.1053 | 39.1053 | 31.1053 | 24.1053 | 24.1053 | 60.4269 | 47.0702 | 64.2251 | 64.2251 | 59.2251 | 54.2251 | 53.2251 | 50.2251 | 41.2251 | 36.2251 | 68.2769 | 58.3398 | 55.7211 | 54.7211 | 49.7211 | 36.7211 | 33.7211 | 32.7211 | 23.7211 | 22.7211 | 58.882 | 44.5689 | 40.5895 | 46.6101 | -70.406 | A+ |  | - | - | - | - | - | - | - | - | - | - | 303.7953 | 1241 | #REF! | Power supply: 230 V, 50 Hz, max 2 kW | 472.5 | 472.5 | 137.8125 | 137.8125 | 153.8% | 158.3% |  |  | 4.2808 | 4.0011 |  |  | Tulosteeseen |  |  |  | 0.831 | 0.86975 | 2000
|  | T | [81 empty] | 131.25 | 131.25
|  |  | Vesipatteri |  |  | 1 | 2 | 3 | 4 | 5
|  | Valittuna | TRUE | [5 empty] | Model 250 | Model 350 |  | Tulosteeseen |  |  |  |  | SPI
|  |  | Menoveden lämpötila |  |  | - | - | - | 50 | 50 |  | - | - |  | Tulosteeseen |  | 0.28493
|  |  | Paluuveden lämpötila |  |  | - | - | - | -5.0297 | -15.4661 |  | - | -
|  |  | Virtaama |  |  | - | - | - | 0.0024745 | 0.00208 |  | - | -
|  |  | Painehäviö patt |  |  | - | - | - | 0.017953 | 0.010445 |  | - | -
|  |  | Painehäviö ventt |  |  | - | - | - | 0.0079353 | 0.0056069 |  | - | -
|  |  | Virtausnopeus |  |  | - | - | - | 0.020164 | 0.016949 |  | - | -
[5 empty] | Virhe |  |  |  | TRUE | TRUE |  | 0
|  |  | Menoveden lämpötila |  |  | - | - | - | 14.9703 | 4.5339 |  | - | -
|  |  | Paluuveden lämpötila |  |  | - | - | - | 30 | 30 |  | - | -
|  |  | Virtaama |  |  | - | - | - | -0.00906 | -0.005347 |  | - | -
|  |  | Painehäviö patt |  |  | - | - | - | #NUM! | #NUM! |  | - | -
|  |  | Painehäviö vent |  |  | - | - | - | 0.10638 | 0.037054 |  | - | -
|  |  | Virtausnopeus |  |  | - | - | - | -0.073827 | -0.043572 |  | - | -
[5 empty] | Virhe |  |  |  | TRUE | TRUE |  | 0
Tarvittava teho
570
-
Tekstejä patterimitoitusosioon

## C koodit (hidden)
(A ) Konetyyppi | ( BBB ) Konekoko | ( C ) Kätisyys - Huom! Varmista kanavajärjestys | ( D ) Koneen Automatiikka | ( E ) Suodatus TULO | ( F ) Suodatus POISTO | ( GG ) Jälkilämmityspatteri, sisäinen | ( H ) Jälkilämmityksen ohjaus, sisäinen | ( I ) Jäähdytyspatteri, sisäinen | ( J ) Jäähdytyksen ohjaus, sisäinen jäähdytyspatteri | ( K ) Suodatinvahti* | ( L ) Vakiopainesäätö* | ( M ) Ilmamäärämittaus* | ( N ) Jousipalautteiset sulkupellit | ( O ) Mittausanturit, sisäinen * | ( P ) Energiamittaus ** | ( Q ) Ohjaus1- toimitus irrallaan, asennus työmaalla | ( RR ) Ohjaus2- toimitus irrallaan, asennus työmaalla | ( S ) Lisäinfo
2 = C = Commercial AHU, Counter-Flow Heat Exchanger | 005, 500dm³/s…1800m³/h (Device: Airfi Model C5 Electric, 230VAC 50Hz 16A, max input power 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max input power 2 kW ) | 1 = R = right (Exhaust air on the right side when viewed from the service side), Standard delivery unless otherwise specified | 1 = Airfi automation, pre-configured with, for example, ModBus RTU/TCP. Versatile connection options, etc. Standard delivery unless otherwise specified. | 5 = ISO ePM10 50% (M5 level) | 5 = ISO ePM10 50%, (Standard delivery in C series unless otherwise specified) (Previous classification: M5 level) | 11 = Electric, Post-heating package 1: Fuse size 400 VAC 3x16A, maximum input power 7.2 kW – Separate power supply for post-heating (for models C5) | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified. | 0 = No internal cooling. Standard delivery unless otherwise specified. | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. | 0 = No filter monitors. Standard delivery unless otherwise specified. | 0 = No constant pressure regulators. Standard delivery unless otherwise specified. | 0 = No air volume flow measurement. Standard delivery unless otherwise specified. | 0 = No dampers or actuators for exhaust and outdoor air. Standard delivery unless otherwise specified. | 0 = No sensors. Standard delivery unless otherwise specified. | 0 = No energy meters. Standard delivery unless otherwise specified. | 0 = No controller. Standard delivery for terminal block units; no other option available. | 00 = Default (not selected). Standard delivery unless otherwise specified. | 1 = Separately specified function; documentation is required as an attachment.
| 0xx, xxxdm³/s…xxxxm³/h (Future version) | 2 = L = left (Exhaus air on the left side when viewed from the service side) | 2 = Terminal block version, with actuators wired to the terminal block. Includes, for example, 5 temperature sensors (NTC) and, in the water model, additionally 1 frost protection sensor (NTC). Also includes transmitters according to the selection of the code key. Delivery does not include control regulators. | 6 = ISO ePM1 65%, (Standard delivery in C series unless otherwise specified) (Previous classification: F7 level) | 6 = ISO ePM1 65% (F7 level) | 12 = Electric, Post-heating package 2: Fuse size 400 VAC 3x25A, maximum input power 14.4 kW – Separate power supply for post-heating (for models C5, Cxx). Standard delivery for unit size C5 Electric unless otherwise specified. | 5 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified. | 1 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 7/12 – 10/15 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 1 = Supply air filter monitor | 1 = Constant pressure regulators for supply and exhaust air (pressure control measurement points to be connected on-site). | 1 = Available starting Q2/2025 – Air volume flow measurement for supply and exhaust air. | 1 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. CAT4 class. | 0 = No sensors. Standard delivery unless otherwise specified. | 1 = Energy meter for operating electricity (fan energy and automation). |  | 00 = Default (not selected). Standard delivery unless otherwise specified. | 2 = Additional time button (installation and wiring by the electrical contractor).
| 0xx, xxxdm³/s…xxxxm³/h (Future version) |  |  | 7 = ISO ePM1 85% (F8/F9 level) | 7 = ISO ePM1 85% (F8/F9 level) | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified. | 7 = Available starting Q3/2025, Water – Post-heating pump unit for 50/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Cooling, liquid – Coil capacity 2, e.g., 10/18 – district cooling/ground cooling system (dimensioning in the program). | 6 = Available starting Q3/2025, Cooling – Pump unit for 7/12 – 10/15, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Exhaust air filter monitor |  |  | 2 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 0 = No sensors. Standard delivery unless otherwise specified. | 2 = Energy meter for operating electricity (fan energy and automation), with an additional energy consumption measurement for electric post-heating units. |  | 00 = Default (not selected). Standard delivery unless otherwise specified. | 9 = Delivery according to the specification list
[6 empty] | 62 = Water – For low temperatures, e.g., 35/25 – 35/30 (dimensioning in the program). |  | 7 = Cooling, direct expansion coil DX-1 (dimensioning in the program). The delivery includes the coil but no actuators. |  | 3 = Supply and exhaust air filter monitors |  |  | 3 = Damper with a spring-return actuator for outdoor air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 0 = No sensors. Standard delivery unless otherwise specified. |  |  | 00 = Default (not selected). Standard delivery unless otherwise specified.
[13 empty] | 4 = Damper with a spring-return actuator for exhaust air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 0 = No sensors. Standard delivery unless otherwise specified. |  |  | 00 = Default (not selected). Standard delivery unless otherwise specified.
5 = Dampers (1 pc for outdoor air + 1 pc for exhaust air), NO ACTUATORS. CAT4 class.
6 = Damper for outdoor air (1 pc), NO ACTUATOR. CAT4 class.
7 = Damper for exhaust air (1 pc), NO ACTUATOR. CAT4 class.
Valinta
1 | 1 | 2 | 2 | 3 | 1 | 3 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3
|  |  |  | ISO ePM1 85% | ISO ePM10 50%
KOODI | [6 empty] | Huom. Vaihtuu valinnan mukaan |  | Huom. Vaihtuu valinnan mukaan |  |  |  |  | Huom. Vaihtuu valinnan mukaan |  | Huom. Vaihtuu valinnan mukaan | Huom. Vaihtuu valinnan mukaan
2 | 005 | 1 | 1 | 5 | 5 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 00 | 1
| 0xx | 2 | 2 | 6 | 6 | 12 | 5 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 |  | 00 | 2
| 0xx |  |  | 7 | 7 | 61 | 7 | 2 | 6 | 2 |  |  | 2 | 0 | 2 |  | 00 | 9
[6 empty] | 62 |  | 7 |  | 3 |  |  | 3 | 0 |  |  | 00
[13 empty] | 4 | 0 |  |  | 00
5
6
7
[14 empty] | 7.1.2025 sähköpostin mukaisesti |  |  | 7.1.2025 sähköpostin mukaisesti
| Perustieto |  |  |  |  | Perustieto | [7 empty] | riviliitinvalinta pakottaa tähän 0 |  |  | riviliitinvalinta pakottaa tähän 0
| 5 |  |  |  |  | Water
Alkuperäiset valikot ja kielivalinta
2 = C = Commercial AHU, Counter-Flow Heat Exchanger | 005, 500dm³/s…1800m³/h (Device: Airfi Model C5 Electric, 230VAC 50Hz 16A, max input power 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max input power 2 kW ) | 1 = R = right (Exhaust air on the right side when viewed from the service side), Standard delivery unless otherwise specified | 1 = Airfi automation, pre-configured with, for example, ModBus RTU/TCP. Versatile connection options, etc. Standard delivery unless otherwise specified. | 5 = ISO ePM10 50% (M5 level) | 5 = ISO ePM10 50%, (Standard delivery in C series unless otherwise specified) (Previous classification: M5 level) | 11 = Electric, Post-heating package 1: Fuse size 400 VAC 3x16A, maximum input power 7.2 kW – Separate power supply for post-heating (for models C5) | 1 = Electric – Standard equipment according to the selected power class (Note: Electric models have a separate power supply for post-heating). | 0 = No internal cooling. Standard delivery unless otherwise specified. | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. | 0 = No filter monitors. Standard delivery unless otherwise specified. | 0 = No constant pressure regulators. Standard delivery unless otherwise specified. | 0 = No air volume flow measurement. Standard delivery unless otherwise specified. | 0 = No dampers or actuators for exhaust and outdoor air. Standard delivery unless otherwise specified. | 0 = No sensors. Standard delivery unless otherwise specified. | 0 = No energy meters. Standard delivery unless otherwise specified. | 0 = No controller. Standard delivery for terminal block units; no other option available. | 00 = Default (not selected). Standard delivery unless otherwise specified. | 1 = Separately specified function; documentation is required as an attachment.
| 0xx, xxxdm³/s…xxxxm³/h (Future version) | 2 = L = left (Exhaus air on the left side when viewed from the service side) | 2 = Terminal block version, with actuators wired to the terminal block. Includes, for example, 5 temperature sensors (NTC) and, in the water model, additionally 1 frost protection sensor (NTC). Also includes transmitters according to the selection of the code key. Delivery does not include control regulators. | 6 = ISO ePM1 65%, (Standard delivery in C series unless otherwise specified) (Previous classification: F7 level) | 6 = ISO ePM1 65% (F7 level) | 12 = Electric, Post-heating package 2: Fuse size 400 VAC 3x25A, maximum input power 14.4 kW – Separate power supply for post-heating (for models C5, Cxx). Standard delivery for unit size C5 Electric unless otherwise specified. | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified. | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified. | 1 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 7/12 – 10/15 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 1 = Supply air filter monitor | 1 = Constant pressure regulators for supply and exhaust air (pressure control measurement points to be connected on-site). | 1 = Available starting Q2/2025 – Air volume flow measurement for supply and exhaust air. | 1 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. CAT4 class. | 1 = RH transmitter | 1 = Energy meter for operating electricity (fan energy and automation). | 8 = Mille Wire (standard delivery includes 1 pc in C-series units). | 01 =Uno White | 2 = Additional time button (installation and wiring by the electrical contractor).
| 0xx, xxxdm³/s…xxxxm³/h (Future version) |  |  | 7 = ISO ePM1 85% (F8/F9 level) | 7 = ISO ePM1 85% (F8/F9 level) | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified. | 5 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Cooling, liquid – Coil capacity 2, e.g., 10/18 – district cooling/ground cooling system (dimensioning in the program). | 2 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 10/18 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Exhaust air filter monitor |  |  | 2 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 2 = CO2 transmitter | 2 = Energy meter for operating electricity (fan energy and automation), with an additional energy consumption measurement for electric post-heating units. |  | 03 =Sento White | 9 = Delivery according to the specification list
[6 empty] | 62 = Water – For low temperatures, e.g., 35/25 – 35/30 (dimensioning in the program). | 6 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 35/25 – 35/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 7 = Cooling, direct expansion coil DX-1 (dimensioning in the program). The delivery includes the coil but no actuators. | 6 = Available starting Q3/2025, Cooling – Pump unit for 7/12 – 10/15, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | 3 = Supply and exhaust air filter monitors |  |  | 3 = Damper with a spring-return actuator for outdoor air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 3 = RH + CO2 transmitter |  |  | 04 = Sento Black
[7 empty] | 7 = Available starting Q3/2025, Water – Post-heating pump unit for 50/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  | 7 = Available starting Q3/2025, Cooling – Pump unit for 10/18, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  |  |  | 4 = Damper with a spring-return actuator for exhaust air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 5 = Available starting 3/2025, Airfi Multisensor (only with Airfi automation). The parameter to be used is selected from the controller. |  |  | 07 =Mille Wifi
[7 empty] | 8 = Available starting Q3/2025, Water – Post-heating pump unit for 35/25 – 35/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | [5 empty] | 5 = Dampers (1 pc for outdoor air + 1 pc for exhaust air), NO ACTUATORS. CAT4 class.
6 = Damper for outdoor air (1 pc), NO ACTUATOR. CAT4 class.
7 = Damper for exhaust air (1 pc), NO ACTUATOR. CAT4 class.
Vaihtoehtovalikot 1 | [6 empty] | GG valinta sähkö |  | I valinta 0,6 tai 7 |  |  |  |  | D valinta 1 |  | D valinta 1 | D valinta 1
[7 empty] | 1 = Electric – Standard equipment according to the selected power class (Note: Electric models have a separate power supply for post-heating). |  | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. |  |  |  |  | 0 = No sensors. Standard delivery unless otherwise specified. |  | 8 = Mille Wire (standard delivery includes 1 pc in C-series units). | 00 = Default (not selected). Standard delivery unless otherwise specified.
[7 empty] | 1 = Electric – Standard equipment according to the selected power class (Note: Electric models have a separate power supply for post-heating). |  | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. |  |  |  |  | 1 = RH transmitter |  |  | 01 =Uno White
[7 empty] | 1 = Electric – Standard equipment according to the selected power class (Note: Electric models have a separate power supply for post-heating). |  | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. |  |  |  |  | 2 = CO2 transmitter |  |  | 03 =Sento White
[14 empty] | 3 = RH + CO2 transmitter |  |  | 04 = Sento Black
[14 empty] | 5 = Available starting 3/2025, Airfi Multisensor (only with Airfi automation). The parameter to be used is selected from the controller. |  |  | 07 =Mille Wifi
Vaihtoehtovalikot 2 | [6 empty] | GG valinta 61 |  | I valinta 1 |  |  |  |  | D valinta 2 |  | D valinta 2 | D valinta 1
[7 empty] | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified. |  | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. |  |  |  |  | 0 = No sensors. Standard delivery unless otherwise specified. |  | 0 = No controller. Standard delivery for terminal block units; no other option available. | 00 = Default (not selected). Standard delivery unless otherwise specified.
[7 empty] | 5 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. |  | 1 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 7/12 – 10/15 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. |  |  |  |  | 0 = No sensors. Standard delivery unless otherwise specified. |  |  | 00 = Default (not selected). Standard delivery unless otherwise specified.
[7 empty] | 7 = Available starting Q3/2025, Water – Post-heating pump unit for 50/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  | 6 = Available starting Q3/2025, Cooling – Pump unit for 7/12 – 10/15, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  |  |  |  | 0 = No sensors. Standard delivery unless otherwise specified. |  |  | 00 = Default (not selected). Standard delivery unless otherwise specified.
[14 empty] | 0 = No sensors. Standard delivery unless otherwise specified. |  |  | 00 = Default (not selected). Standard delivery unless otherwise specified.
[14 empty] | 0 = No sensors. Standard delivery unless otherwise specified. |  |  | 00 = Default (not selected). Standard delivery unless otherwise specified.
Vaihtoehtovalikot 3 | [6 empty] | GG valinta 62 |  | I valinta 1
[7 empty] | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified. |  | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified.
[7 empty] | 6 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 35/25 – 35/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. |  | 2 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 10/18 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready.
[7 empty] | 8 = Available starting Q3/2025, Water – Post-heating pump unit for 35/25 – 35/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  | 7 = Available starting Q3/2025, Cooling – Pump unit for 10/18, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready.
#VALUE!
#VALUE!
Valinnat
A
| 1 | 2 = C = Commercial AHU, Counter-Flow Heat Exchanger | 2
B
| 1 | 005, 500dm³/s…1800m³/h (Device: Airfi Model C5 Electric, 230VAC 50Hz 16A, max input power 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max input power 2 kW ) | 005
C
| 2 | 2 = L = left (Exhaus air on the left side when viewed from the service side) | 2
D
| 2 | 2 = Terminal block version, with actuators wired to the terminal block. Includes, for example, 5 temperature sensors (NTC) and, in the water model, additionally 1 frost protection sensor (NTC). Also includes transmitters according to the selection of the code key. Delivery does not include control regulators. | #VALUE!
E
| 3 | 7 = ISO ePM1 85% (F8/F9 level) | 7
F
| 1 | 5 = ISO ePM10 50%, (Standard delivery in C series unless otherwise specified) (Previous classification: M5 level) | 5
G
| 3 | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified. | 61
H
| 1 | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified. | 3
I
| 2 | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified. | 1
J
| 1 | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. | 0
K
| 1 | 0 = No filter monitors. Standard delivery unless otherwise specified. | 0
L
| 1 | 0 = No constant pressure regulators. Standard delivery unless otherwise specified. | 0
M
| 1 | 0 = No air volume flow measurement. Standard delivery unless otherwise specified. | 0
| N | [9 empty] | Sähköposti 7.1.2025
| 1 | 0 = No dampers or actuators for exhaust and outdoor air. Standard delivery unless otherwise specified. | 0
O
| 1 | 0 = No sensors. Standard delivery unless otherwise specified. | 0
P
| 1 | 0 = No energy meters. Standard delivery unless otherwise specified. | 0
Q
| 1 | 0 = No controller. Standard delivery for terminal block units; no other option available. | 0
R
| 1 | 00 = Default (not selected). Standard delivery unless otherwise specified. | 00
S
| 3 | 9 = Delivery according to the specification list | 9
Valitut suodattimet:
| Tulo: | ISO ePM1 85%
| Poisto: | ISO ePM10 50%
Valitut suodattimet: Tulo: ISO ePM1 85% Poisto: ISO ePM10 50%
| Perustieto: | Airfi Model C5 Water

## KirjastoC_koodit (hidden)
Kieli | 2
| SUOMI | [18 empty] | VALINTA
| 2 = C = Commercial AHU, LTO-Vastavirtasiirrin | 005, 500dm³/s…1800m³/h (Kone: Airfi Model C5 Electric, 230VAC 50Hz 16A, max ottoteho 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max ottoteho 2 kW ) | 1 = R = oikea (jäteilma oikeassa reunassa huoltosuunnasta katsoen), Vakiotoimitus, jos ei muuta pyydetty | 1 = Airfi automatiikka, valmiina mm. ModBus RTU/TCP . Monipuoliset kytkentä mahdollisuudet jne… Vakiotoimitus jos ei muuta pyydetty. | 5 = ISO ePM10 50% (M5 taso) | 5 = ISO ePM10 50%, (Vakiotoimitus C-koneissa, jos ei valittu muuta) (aiempi luokitus M5-taso) | 11 = Electric, Jälkilämmityspaketti 1: Sulakekoko 400VAC 3x16A, max ottoteho 7,2 kW - Oma jälkilämmityksen syöttö (malleihin C5) | 1 = Electric, Vakiona valitun teholuokan mukaiset varusteet (Huom! Electric malleissa jälkilämmityksen oma sähkönsyöttö) | 0 = ei sisäistä jäähdytystä. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei jäähdytyksen toimilaitteita tai venttiileitä. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei suodatinvahteja. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei vakiopainesäätöä. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei ilmamäärämittausta. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei sulkupeltejä eikä toimilaitteita jäte- ja ulkoilmalle. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei sensoreita. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei energiamittareita. Vakiotoimitus jos ei muuta pyydetty. | 0 = Ei ohjainta, Vakiotoimitus riviliitinkoneessa, ei voi valita muuta | 00 = Oletus (ei valittu), Vakiotoimitus jos ei muuta pyydetty) | 1 = Erikseen selvitetty toiminto, dokumentaatio vaaditaan liitteeksi. | 2 = C = Commercial AHU, Counter-Flow Heat Exchanger | 005, 500dm³/s…1800m³/h (Device: Airfi Model C5 Electric, 230VAC 50Hz 16A, max input power 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max input power 2 kW ) | 1 = R = right (Exhaust air on the right side when viewed from the service side), Standard delivery unless otherwise specified | 1 = Airfi automation, pre-configured with, for example, ModBus RTU/TCP. Versatile connection options, etc. Standard delivery unless otherwise specified. | 5 = ISO ePM10 50% (M5 level) | 5 = ISO ePM10 50%, (Standard delivery in C series unless otherwise specified) (Previous classification: M5 level) | 11 = Electric, Post-heating package 1: Fuse size 400 VAC 3x16A, maximum input power 7.2 kW – Separate power supply for post-heating (for models C5) | 1 = Electric – Standard equipment according to the selected power class (Note: Electric models have a separate power supply for post-heating). | 0 = No internal cooling. Standard delivery unless otherwise specified. | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. | 0 = No filter monitors. Standard delivery unless otherwise specified. | 0 = No constant pressure regulators. Standard delivery unless otherwise specified. | 0 = No air volume flow measurement. Standard delivery unless otherwise specified. | 0 = No dampers or actuators for exhaust and outdoor air. Standard delivery unless otherwise specified. | 0 = No sensors. Standard delivery unless otherwise specified. | 0 = No energy meters. Standard delivery unless otherwise specified. | 0 = No controller. Standard delivery for terminal block units; no other option available. | 00 = Default (not selected). Standard delivery unless otherwise specified. | 1 = Separately specified function; documentation is required as an attachment.
|  | 0xx, xxxdm³/s…xxxxm³/h (Future version) | 2 = L = vasen (jäteilma vasemmassa reunassa huoltosuunnasta katsoen) | 2 = Rivilitinversio, toimilaitteet johdotettu riviliittimelle. Sisältää mm. 5 kpl lämpötila-anturi NTC, ja vesimallissa lisäksi 1 kpl jäätymissuoja-anturi NTC. Sekä koodiavaimen valintojen mukaisesti lähettimet. Toimitus ei sisällä ohjaussäätimiä. | 6 = ISO ePM1 65%, (Vakiotoimitus C-koneissa, jos ei valittu muuta) (aiempi luokitus F7 taso) | 6 = ISO ePM1 65% (F7-taso) | 12 = Electric, Jälkilämmityspaketti 2: Sulakekoko 400VAC 3x25A, max ottoteho 14,4 kW - Oma jälkilämmityksen syöttö (malleihin C5, Cxx), Vakiotoimitus konekoossa C5 Electric jos ei muuta pyydetty | 3 = Water , Toimituksessa ei mukana vesipatterin toimilaitteita tai venttiileitä - Vakiotoimitus C-sarjan Water -koneissa jos ei muuta pyydetty. | 1 = Jäähdytys neste, patteriteho 1 ,esim. 7/12 - 10/15 (mitoita ohjelmassa). Vakiotoimitus C-sarjassa jos valittu jäähdytyspatteri ja ei muuta pyydetty | 1 = Toim. alk. Q3/2025, Jäähdytyksen 3- tieventtiili ja toimilaite - patterin 7/12 - 10/15 mukaan (toimitus irrallaan, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis. | 1 = Suodatinvahti tulo | 1 = Vakiopainesäätö tulo ja poisto (vakiopainesäädön mittauspisteet letkutetaan työmaalla) | 1 = Toim. alk. Q2/2025 - Ilmavirtamittaus tulo- ja poistoilmavirralle | 1 = Sulkupellit sekä jousipalautteiset toimilaitteet (1kpl ulkoilma + 1 kpl jäteilma), valmiiksi tehtaalla sähköisesti kytketty . CAT4 luokka. | 1 = RH - lähetin | 1 = Energiamittari käyttösähkö (puhallinenergia ja automaatio) | 8 = Mille Wire (vakiona toimituksessa C-sarjan koneissa 1 kpl) | 01 =Uno White | 2 = Lisäaikapainike (asennus ja johdotus SU) |  | 0xx, xxxdm³/s…xxxxm³/h (Future version) | 2 = L = left (Exhaus air on the left side when viewed from the service side) | 2 = Terminal block version, with actuators wired to the terminal block. Includes, for example, 5 temperature sensors (NTC) and, in the water model, additionally 1 frost protection sensor (NTC). Also includes transmitters according to the selection of the code key. Delivery does not include control regulators. | 6 = ISO ePM1 65%, (Standard delivery in C series unless otherwise specified) (Previous classification: F7 level) | 6 = ISO ePM1 65% (F7 level) | 12 = Electric, Post-heating package 2: Fuse size 400 VAC 3x25A, maximum input power 14.4 kW – Separate power supply for post-heating (for models C5, Cxx). Standard delivery for unit size C5 Electric unless otherwise specified. | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified. | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified. | 1 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 7/12 – 10/15 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 1 = Supply air filter monitor | 1 = Constant pressure regulators for supply and exhaust air (pressure control measurement points to be connected on-site). | 1 = Available starting Q2/2025 – Air volume flow measurement for supply and exhaust air. | 1 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. CAT4 class. | 1 = RH transmitter | 1 = Energy meter for operating electricity (fan energy and automation). | 8 = Mille Wire (standard delivery includes 1 pc in C-series units). | 01 =Uno White | 2 = Additional time button (installation and wiring by the electrical contractor).
|  | 0xx, xxxdm³/s…xxxxm³/h (Future version) |  |  | 7 = ISO ePM1 85% (F8/F9 taso) | 7 = ISO ePM1 85% (F8/F9 taso) | 61 = Water- soveltuu esim. 50/30 vedelle (mitoita ohjelmassa), Vakiotoimitus mallissa C5 Water jos ei muuta pyydetty | 5 = Toim.alk.Q2/2025, Water , Jälkilämmityksen 2-tieventtiili ja toimilaite - patterin 50/30 mukaan (toimitus irrallaan, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis. | 2 = Jäähdytys neste , patteriteho 2. esim. 10/18 -kaukokylmä/maajärjestelmä (mitoita ohjelmassa) | 2 = Toim. alk. Q3/2025, Jäähdytyksen 3- tieventtiili ja toimilaite - patterin 10/18 mukaan (toimitus irrallaan, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis. | 2 = Suodatinvahti poisto |  |  | 2 = Sulkupellit sekä jousipalautteiset toimilaitteet (1kpl Ulkoilma + 1 kpl jäteilma), valmiiksi tehtaalla sähköisesti kytketty . Eristetyt säleet , CAT 4 luokka. | 2 = CO2 - lähetin | 2 = Energiamittari käyttösähkö (puhallinenergia ja automaatio) ja lisäksi sähkökoneessa erillinen jälkilämmityksen energian kulutusmittaus. |  | 03 =Sento White | 9 = Toimitus listauksen mukaisesti |  | 0xx, xxxdm³/s…xxxxm³/h (Future version) |  |  | 7 = ISO ePM1 85% (F8/F9 level) | 7 = ISO ePM1 85% (F8/F9 level) | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified. | 5 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Cooling, liquid – Coil capacity 2, e.g., 10/18 – district cooling/ground cooling system (dimensioning in the program). | 2 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 10/18 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Exhaust air filter monitor |  |  | 2 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 2 = CO2 transmitter | 2 = Energy meter for operating electricity (fan energy and automation), with an additional energy consumption measurement for electric post-heating units. |  | 03 =Sento White | 9 = Delivery according to the specification list
[7 empty] | 62 = Water- matalille lämpötiloille, esim. 35/25 - 35/30 (mitoita ohjelmassa) | 6 = Toim. alk. Q2/2025, Water , Jälkilämmityksen 2-tieventtiili ja toimilaite - patterin 35/25 - 35/30 mukaan (toimitus irrallaan, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis. | 7 = Jäähdytys suorahöyrystyspatteri DX-1, (mitoita ohjelmassa), toimitus sisältää patterin, ei toimilaitteita | 6 = Toim. alk. Q3/2025, Jäähdytyksen pumppuryhmä 7/12 - 10/15 kasattuna ja eristettynä (toimitus erillispakettina, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis. | 3 = Suodatinvahti tulo ja poisto |  |  | 3 = Sulkupelti sekä jousipalautteinen toimilaite Ulkoilma (1kpl) , valmiiksi tehtaalla sähköisesti kytketty . Eristetyt säleet , CAT 4 luokka. | 3 = RH + CO2 - lähetin |  |  | 04 = Sento Black | [7 empty] | 62 = Water – For low temperatures, e.g., 35/25 – 35/30 (dimensioning in the program). | 6 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 35/25 – 35/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 7 = Cooling, direct expansion coil DX-1 (dimensioning in the program). The delivery includes the coil but no actuators. | 6 = Available starting Q3/2025, Cooling – Pump unit for 7/12 – 10/15, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | 3 = Supply and exhaust air filter monitors |  |  | 3 = Damper with a spring-return actuator for outdoor air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 3 = RH + CO2 transmitter |  |  | 04 = Sento Black
[8 empty] | 7 = Toim. alk. Q3/2025, Water , Jälkilämmityksen pumppuryhmä 50/30 kasattuna ja eristettynä (toimitus erillispakettina, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis |  | 7 = Toim. alk. Q3/2025, Jäähdytyksen pumppuryhmä 10/18 kasattuna ja eristettynä (toimitus erillispakettina, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis. |  |  |  | 4 = Sulkupelti sekä jousipalautteinen toimilaite Jäteilma (1kpl), valmiiksi tehtaalla sähköisesti kytketty . Eristetyt säleet , CAT 4 luokka. | 5 = Toim. alk. 3/2025 , Airfi Multisensor (vain Airfi automatiikassa) , säätimeltä valitaan mitä suuretta käytetään. |  |  | 07 =Mille Wifi | [8 empty] | 7 = Available starting Q3/2025, Water – Post-heating pump unit for 50/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  | 7 = Available starting Q3/2025, Cooling – Pump unit for 10/18, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  |  |  | 4 = Damper with a spring-return actuator for exhaust air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 5 = Available starting 3/2025, Airfi Multisensor (only with Airfi automation). The parameter to be used is selected from the controller. |  |  | 07 =Mille Wifi
[8 empty] | 8 = Toim. alk. Q3/2025, Water , Jälkilämmityksen pumppuryhmä 35/25 - 35/30 kasattuna ja eristettynä (toimitus erillispakettina, kytkentä ja asennus PU). Sähköisesti Plug&Play valmis | [5 empty] | 5 = Sulkupellit (1kpl Ulkoilma + 1 kpl jäteilma), EI TOIMILAITTEITA. CAT 4 luokka. | [12 empty] | 8 = Available starting Q3/2025, Water – Post-heating pump unit for 35/25 – 35/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | [5 empty] | 5 = Dampers (1 pc for outdoor air + 1 pc for exhaust air), NO ACTUATORS. CAT4 class.
[14 empty] | 6 = Sulkupelti Ulkoilma (1kpl), EI TOIMILAITETTA. CAT 4 luokka. | [18 empty] | 6 = Damper for outdoor air (1 pc), NO ACTUATOR. CAT4 class.
[14 empty] | 7 = Sulkupelti Jäteilma (1kpl), EI TOIMILAITETTA. CAT 4 luokka. | [18 empty] | 7 = Damper for exhaust air (1 pc), NO ACTUATOR. CAT4 class.
ENGLANTI
| 2 = C = Commercial AHU, Counter-Flow Heat Exchanger | 005, 500dm³/s…1800m³/h (Device: Airfi Model C5 Electric, 230VAC 50Hz 16A, max input power 2 kW / Airfi Model C5 Water, 230VAC 50Hz 16A, max input power 2 kW ) | 1 = R = right (Exhaust air on the right side when viewed from the service side), Standard delivery unless otherwise specified | 1 = Airfi automation, pre-configured with, for example, ModBus RTU/TCP. Versatile connection options, etc. Standard delivery unless otherwise specified. | 5 = ISO ePM10 50% (M5 level) | 5 = ISO ePM10 50%, (Standard delivery in C series unless otherwise specified) (Previous classification: M5 level) | 11 = Electric, Post-heating package 1: Fuse size 400 VAC 3x16A, maximum input power 7.2 kW – Separate power supply for post-heating (for models C5) | 1 = Electric – Standard equipment according to the selected power class (Note: Electric models have a separate power supply for post-heating). | 0 = No internal cooling. Standard delivery unless otherwise specified. | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified. | 0 = No filter monitors. Standard delivery unless otherwise specified. | 0 = No constant pressure regulators. Standard delivery unless otherwise specified. | 0 = No air volume flow measurement. Standard delivery unless otherwise specified. | 0 = No dampers or actuators for exhaust and outdoor air. Standard delivery unless otherwise specified. | 0 = No sensors. Standard delivery unless otherwise specified. | 0 = No energy meters. Standard delivery unless otherwise specified. | 0 = No controller. Standard delivery for terminal block units; no other option available. | 00 = Default (not selected). Standard delivery unless otherwise specified. | 1 = Separately specified function; documentation is required as an attachment.
|  | 0xx, xxxdm³/s…xxxxm³/h (Future version) | 2 = L = left (Exhaus air on the left side when viewed from the service side) | 2 = Terminal block version, with actuators wired to the terminal block. Includes, for example, 5 temperature sensors (NTC) and, in the water model, additionally 1 frost protection sensor (NTC). Also includes transmitters according to the selection of the code key. Delivery does not include control regulators. | 6 = ISO ePM1 65%, (Standard delivery in C series unless otherwise specified) (Previous classification: F7 level) | 6 = ISO ePM1 65% (F7 level) | 12 = Electric, Post-heating package 2: Fuse size 400 VAC 3x25A, maximum input power 14.4 kW – Separate power supply for post-heating (for models C5, Cxx). Standard delivery for unit size C5 Electric unless otherwise specified. | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified. | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified. | 1 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 7/12 – 10/15 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 1 = Supply air filter monitor | 1 = Constant pressure regulators for supply and exhaust air (pressure control measurement points to be connected on-site). | 1 = Available starting Q2/2025 – Air volume flow measurement for supply and exhaust air. | 1 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. CAT4 class. | 1 = RH transmitter | 1 = Energy meter for operating electricity (fan energy and automation). | 8 = Mille Wire (standard delivery includes 1 pc in C-series units). | 01 =Uno White | 2 = Additional time button (installation and wiring by the electrical contractor).
|  | 0xx, xxxdm³/s…xxxxm³/h (Future version) |  |  | 7 = ISO ePM1 85% (F8/F9 level) | 7 = ISO ePM1 85% (F8/F9 level) | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified. | 5 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Cooling, liquid – Coil capacity 2, e.g., 10/18 – district cooling/ground cooling system (dimensioning in the program). | 2 = Available starting Q3/2025, Cooling – 3-way valve and actuator for a coil with 10/18 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 2 = Exhaust air filter monitor |  |  | 2 = Dampers with spring-return actuators (1 pc for outdoor air + 1 pc for exhaust air), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 2 = CO2 transmitter | 2 = Energy meter for operating electricity (fan energy and automation), with an additional energy consumption measurement for electric post-heating units. |  | 03 =Sento White | 9 = Delivery according to the specification list
[7 empty] | 62 = Water – For low temperatures, e.g., 35/25 – 35/30 (dimensioning in the program). | 6 = Available starting Q2/2025, Water – 2-way valve and actuator for post-heating, designed for a coil with 35/25 – 35/30 specifications (delivered separately, connection and installation by the main contractor). Electrically Plug & Play ready. | 7 = Cooling, direct expansion coil DX-1 (dimensioning in the program). The delivery includes the coil but no actuators. | 6 = Available starting Q3/2025, Cooling – Pump unit for 7/12 – 10/15, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | 3 = Supply and exhaust air filter monitors |  |  | 3 = Damper with a spring-return actuator for outdoor air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 3 = RH + CO2 transmitter |  |  | 04 = Sento Black
[8 empty] | 7 = Available starting Q3/2025, Water – Post-heating pump unit for 50/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  | 7 = Available starting Q3/2025, Cooling – Pump unit for 10/18, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. |  |  |  | 4 = Damper with a spring-return actuator for exhaust air (1 pc), electrically pre-wired at the factory. Insulated blades, CAT4 class. | 5 = Available starting 3/2025, Airfi Multisensor (only with Airfi automation). The parameter to be used is selected from the controller. |  |  | 07 =Mille Wifi
[8 empty] | 8 = Available starting Q3/2025, Water – Post-heating pump unit for 35/25 – 35/30, assembled and insulated (delivered as a separate package, connection and installation by the main contractor). Electrically Plug & Play ready. | [5 empty] | 5 = Dampers (1 pc for outdoor air + 1 pc for exhaust air), NO ACTUATORS. CAT4 class.
6 = Damper for outdoor air (1 pc), NO ACTUATOR. CAT4 class.
7 = Damper for exhaust air (1 pc), NO ACTUATOR. CAT4 class.

## SEC-laskenta_C (hidden)
SEC-laskenta
[6 empty] | SEC | -70.406 |  |  |  | Vertailuarvo |  | -70.406 | A+
General typology | MISC |  | Valinta | MISC
Ducted units | 1.1 |  | 2 | 1.21 | [6 empty] | A+ |  | -42 | 0
Non-ducted units | 1.21 | [9 empty] | A | -42 | -34 | 0
[11 empty] | B | -34 | -26 | 0
Ventilation control | CTRL |  | Valinta | CTRL | [6 empty] | C | -26 | -23 | 0 | Specific energy consumption (SEC) and classification | [6 empty] | Class | SEC-value
Manual control (no DCV) | 1 |  | 1 | 1 | [6 empty] | D | -23 | -20 | 0 | According to Commission Regulations (EU) No 1253/2014 & No 1254/2014 | [5 empty] | ► | A+ | SEC < -42
Clock control (no DCV) | 0.95 | [9 empty] | E | -20 | -10 | 0 | NB! SEC-calculation is only used for air handling units intended for residential buildings | [6 empty] | A | -42 < SEC < -34
Central demand control | 0.85 | [9 empty] | F | -10 | 0 | 0 | Reference air flow: | 1386 | [5 empty] | B | -34 < SEC < -26
Local demand control | 0.65 | [9 empty] | G | 0 |  | 0 | Calculation parameters: | [6 empty] | C | -26 < SEC < -23
[15 empty] | General typology |  |  |  | SEC-value | -70.406 |  | D | -23 < SEC < -20
Motor & drive | x-value |  | Valinta | x-value | [10 empty] | Ventilation control |  |  |  | [kWh / (a·m2)] |  |  | E | -20 < SEC < -10
On/off & single speed | 1 |  | 2 | 1.2 | [10 empty] | Motor & drive |  |  |  | Class | A+ |  | F | -10 < SEC < 0
2-speed | 1.2 | [13 empty] | Climate | [6 empty] | G | SEC > 0
Multi-speed | 1.5 | [13 empty] | All rights reserved. |  | www.airfi.fi | www.airfi.eu
Variable-speed | 2 | [13 empty] | Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program.
Climate | th | ΔTh | tdefr | ΔTdefr | Qdefr | Valinta | th | ΔTh | tdefr | ΔTdefr | Qdefr |  |  |  | The selection program is made by Zenner Engineers. The program is based on laboratory measurements according to SFS-EN 13141-7.
Cold | 6552 | 14.5 | 1003 | 5.2 | 5.82 | 1 | 6552 | 14.5 | 1003 | 5.2 | 5.82
Average | 5112 | 9.5 | 168 | 2.4 | 0.45
Warm | 4392 | 5
Defaults | Value
cair | 0.000344
qnet | 1.3
qref | 2.2
ta | 8760
pef | 2.5
ηh | 0.75
ηt | 0.85285
SFP | 0.99834 | kW/(m3/s)
SPI | 0.00027732 | kW/(m3/h)

## Kojeet ja kennon hyötysuhde_C (hidden)
[8 empty] | Vanha | [7 empty] | LTO-arvot A. Pulkkasen sähköpostilla antaman ehdotuksen mukaisesti (8.2.2024)
Kojevalinta | 1 |  | Tunnus | Malli | Min. qV | Maks. qV | Jäteilman raj. | n, tulo | EN 13141-7 | EN 308 |  |  | Laskentaohjelmaan | Laskentaohjelmaan |  | Laskentaohjelmassa V. 5,8 | [7 empty] | AIEMMAT ARVOT |  |  |  | Ehdotus
Jäteilma | -6.5 |  | 1 | C5 | 100 | 700 | -6.5 | 82% | 83.1% | 86.98% | [17 empty] | versio 5.9 ja seuraavat
Min. qV | 100 |  | 2 | [5 empty] | - | - |  |  |  |  | Recutech ohjelmasta
Maks. qV | 700 |  | 3 | [5 empty] | - | - |  |  | EHDOTUS | EHDOTUS | alla kuvakaappaukset että jää jälki mihin perustuu |  | Ohjelmassa NRLTO=1, nyt
n, tulostus | 82% |  | 4 | [5 empty] | - | - | dm3/s | ZENNER - Mitattu tuloilman lämpötilahyötysuhde 1:1 | Tuloilman lämpötilahyötysuhde yhtä suurilla ilmavirroilla (EN 13141-7) | Lämmöntalteenottokennon hyötysuhde (EN308)* | Kenno EN308
[11 empty] | 100 |  | 83 | 87 | 91.3
[11 empty] | 200 | 83.4 | 83.4 | 86.9 | 86.9 |  | Model 60, 79,5 % | [5 empty] | Model 60
[11 empty] | 300 | 85.2 | 85.2 | 84 | 84.1 |  | Model 100, 82,5 % | [5 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 60-kone, mitattu Zenner |  |  | dm³/s | Model 60nykyinen NRLTO=1 | EHDOTUS, model 60, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 60
[11 empty] | 400 | 84.1 | 85.3 | 82.2 | 82.2 |  | Model 130, 77,5 % | [6 empty] | 25 |  |  |  | 18 | 79.5 | 79.8 | 81.75
[11 empty] | 500 | 85.3 | 85.3 | 81 | 81 |  | Model 150, 79,5 % | [5 empty] | 3.4 | 34 | 80.1 |  |  | 28 | 79.5 | 79.7 | 81.5
[11 empty] | 600 |  | 85.1 | 79.9 | 79.9 | [7 empty] | 3.8 | 43 | 80.7 |  |  | 36 | 79.5 | 79.6 | 81
[11 empty] | 700 |  | 85 | 79.1 | 79.1 |  | Model 250 ja Model 350 muuttuva | [5 empty] | 5.9 | 74 | 81.5 |  |  | 61.5 | 79.5 | 79.5 | 80.3
[14 empty] | * Komponenttitoimittajan ilmoittama EN308-arvo |  |  |  | ilmavirta | arvo |  |  |  | 9.2 | 108 | 83.1 |  |  | 90 | 79.5 | 78.5 | 79.5
[18 empty] | 50 | 79.5 |  |  |  |  | 130 |  |  |  | 130 | 79.5 | 78 | 78.2
[12 empty] | Ehdot, ei voi laskea ilmavirroille alle 200 dm³/s tätä konetta C5 | [5 empty] | 100 | 79.5 | [8 empty] | 130 | 79.5 | 78 | 78.2
[12 empty] | Ehdot, ei voi laskea yli maksimikäyrän tätä konetta C5 | [5 empty] | 150 | 79.5
[12 empty] | Ehdot, ns Paine-ero tulo --- ei saa laittaa arvoksi yli 500 Pa tulopuolelle (tehostuskäyrä voi laskea vapaasti) | [5 empty] | 200 | 79.3
Laitevalinta | 1 | C5 | [9 empty] | Ehdot, ns Paine-ero--- ei saa laittaa arvoksi yli 500 Pa poistopuolelle (tehostuskäyrä voi laskea vapaasti) | [5 empty] | 250 | 78.2
[18 empty] | 300 | 77.5
[18 empty] | 350 | 77.3 |  |  |  | Model 100
Tilavuusvirta [dm³/s] | Arvo versioon v5.9 saakka | EN 13141-7 Nt(RLTO=1) | EN 308 | [8 empty] | C5 | [10 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 100-kone, mitattu Zenner |  |  | dm³/s | Model 100nykyinen NRLTO=1 | EHDOTUS, model 100, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 100
100 |  | 83% | 87% | [7 empty] | qV | Ilman massavirta | Tuloilman lämpötilahyötysuhde | [10 empty] | 25 |  |  |  | 18 | 82.5 | 82.5 | 84
200 |  | 83.4% | 86.9% | [9 empty] | Kenno (mitattu) | Kenno (valmistajalta) | Kone (Airfi C5) | [7 empty] | 3.6 | 34 | 82.7 |  |  | 29 | 82.5 | 82.5 | 83.7
300 |  | 85.2% | 84% | [7 empty] | 198.8923 | 238.6708 | 81.94% | 87.2% | 83.39% | [7 empty] | 4.2 | 43 | 82.3 |  |  | 36 | 82.5 | 82.5 | 83.5
400 |  | 85.3% | 82.2% | [7 empty] | 302.8176 | 363.3812 | 82.58% | 84.1% | 85.2% | [7 empty] | 6.1 | 71 | 83.2 |  |  | 60 | 82.5 | 82.4 | 83.2
500 |  | 85.3% | 81% | [7 empty] | 401.3018 | 481.5621 | 80.49% | 82.6% | 84.1% | [7 empty] | 9.7 | 107 | 84.8 |  |  | 90 | 82.5 | 81.5 | 82
600 |  | 85.1% | 79.9% | [7 empty] | 496.1342 | 595.361 | 78.96% | 80.3% | 85.33% | [8 empty] | 130 |  |  |  | 130 | 82.5 | 80 | 80.2
700 |  | 85% | 79.1% | [24 empty] | 130 | 82.5 | 80 | 80.2
| qV | EN 13141-7 | EN 308
Min | 100 | 0.83 | 0.87
Max | 700 | 0.853 | 0.822 | [19 empty] | Model 130
[23 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 130-kone, simuloitu |  |  | dm³/s | Model 130nykyinen NRLTO=1 | EHDOTUS, model 130, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 130
Mitoitus qV | 125 | [22 empty] | 25 |  |  |  | 18 | 77.5 | 77.5 | 79.5
Tarkistus min/max | 125 | [22 empty] | 34 | 77.5 |  |  | 29 | 77.5 | 77.5 | 79
EN 13141-7 | 0.831 | 83.1% | [21 empty] | 43 | 77.5 |  |  | 36 | 77.5 | 77.5 | 78.5
EN 308 | 0.86975 | 86.98% | [21 empty] | 71 | 77.5 |  |  | 60 | 77.5 | 77 | 77.5
[24 empty] | 107 | 77.5 |  |  | 90 | 77.5 | 75.5 | 76
[24 empty] | 140 |  |  |  | 140 | 77.5 | 73.5 | 74
Aputaulukko | EN 13141-7 | EN 308 | [25 empty] | 140 | 77.5 | 73.5 | 74
100 | 0.83 | 0.87
200 | 0.834 | 0.869
Model 150
[23 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 150-kone, mitattu Zenner |  |  | dm³/s | Model 150nykyinen NRLTO=1 | EHDOTUS, model 150, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 150
Kielivalinta | [23 empty] | 25 |  |  |  | 18 | 79.5 | 79.5 | 82
Suomi | FALSE | [21 empty] | 3,8/3,8 | 68 | 79.3 |  |  | 29 | 79.5 | 79.5 | 81.75
Muut | TRUE | [21 empty] | 4,6/4,2 | 91 | 79.5 |  |  | 36 | 79.5 | 79.5 | 81.5
[23 empty] | 7,4/6,1 | 127 | 76.6 |  |  | 80 | 79.5 | 79.5 | 80.5
Syöttö | 450 | m³/h | [20 empty] | 10/8 | 167 | 79.9 |  |  | 120 | 79.5 | 79.5 | 80
Laskentaan | 125 | l/s | [21 empty] | 200 |  |  |  | 180 | 79.5 | 79 | 79.5
[25 empty] | ilmeisesti poikkeama kohdassa 76,6 |  |  | 180 | 79.5 | 79 | 79.5
Mitoituspiste: | 550 | dm³/s
EN 1314-7 | 85.2%
EN 308 | 80.45% | [21 empty] | Model 250 / 350
[24 empty] | dm³/s |  |  |  | dm³/s | Model 250-350 nykyinen NRLTO=1 | EHDOTUS, model 250-350, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 250-350
[24 empty] | 50 | 79.5 |  |  | 50 | 79.5 | 79.5 | 81
[24 empty] | 100 | 79.5 |  |  | 100 | 79.5 | 79.5 | 80.5
[24 empty] | 150 | 79.5 |  |  | 150 | 79.5 | 79.5 | 80
[24 empty] | 200 | 79.3 |  |  | 200 | 79.3 | 79 | 79.5
[24 empty] | 250 | 78.2 |  |  | 250 | 78.2 | 78.2 | 78.7
[24 empty] | 300 | 77.5 |  |  | 300 | 77.5 | 77.5 | 78
[24 empty] | 350 | 77.3 |  |  | 350 | 77.3 | 76.8 | 77
Vanhaa laskentaa --> EI KÄYTÖSSÄ
Airfi Model 300
Airfi model 60
LEV-455-230, pituus 350 mm, s=2.3 mm | [20 empty] | Nykyinen MODEL 150 kenno
[21 empty] | ARVOT EKOCOIL OPTIMIZER, LEV-620-394-500-(lamelli 2,2) |  |  |  | MODEL 150 |  | MODEL 300 (nyk kenno)
[22 empty] | LAMELLIVÄLI 2,2 mm |  |  | lamelliväli 2,2 |  | lamelliväli 2,2
Tulko | 7 | 50%RH | [17 empty] | dm3/s | Ilmavirta , m³/s | Hyötysuhde (tulo 2,2), model 150 | Hyötysuhde (poisto) | Painehäviö 2,2 | nykyinen arvo- koneen hyötysuhde MODEL 150 | laskettu- koneen vuosi hyötysuhde MODEL 150 | ajatus koneen lämpötilahyöstysuhde (model 300) | mistä laskettu model 300 vuosihyötysuhde
Tpoisto | 20 | 50%RH | [17 empty] | 50 | 0.05 | 83.5 | 84 | 19 | 79.5 | 76.1 | 79.5 | 76.1
[20 empty] | 75 | 0.075 | 81.5 | 82 | 33 | 79.5 | 76.1 | 79.5 | 76.1
qV | n, tulo | [18 empty] | 100 | 0.1 | 80.2 | 80.7 | 48 | 79.5 | 76.1 | 79.5 | 76.1
100 | 78.1% | [18 empty] | 150 | 0.15 | 78.5 | 78.9 | 85 | 79.5 | 76.1 | 79.5 | 76.1
90 | 78.4% | [18 empty] | 200 | 0.2 | 77.2 | 77.6 | 126 | ei alueella | ei alueella | 77.2 | 74.5
80 | 78.7% | [18 empty] | 250 | 0.25 | 76.2 | 76.7 | 168 | ei alueella | ei alueella | 76.2 | 74.1
70 | 79.1% | [18 empty] | 300 | 0.3 | 75.6 | 76.1 | 231 | ei alueella | ei alueella | 75.6 | 73.6
60 | 79.5% | [18 empty] | 350 | 0.35 | 75.3 | 75.8 | 306 | ei alueella | ei alueella | 75.3 | 73.6
50 | 80.2%
40 | 81.3% | [30 empty] | Käytetään tätä (huom. Versioon 5.9 saakka, tämän jälkeen tuli muutos)
30 | 83.4%
22 | 86.4%
6.6314e-09 | -2.017e-06 | 0.00022914 | -0.011912 | 1.0348 | [23 empty] | Max | 83.5 |  |  |  | Max | 79.5
[28 empty] | Min | 75.3 |  |  |  | Min | 77.26%
qV, tulo
qV, poisto | [27 empty] | -0.054191 | 4.635 | 103.024 |  |  | 7.681e-05 | -0.055722 | 87.3508
qV, mitoitus
n, tulo, mitoitus | [27 empty] | Mitoituspiste, tuloilma |  |  |  |  | Mitoituspiste, tuloilma
[28 empty] | 125 | dm3/s |  |  |  | 125 | dm3/s
Airfi model 100 | [27 empty] | 79.3058 | % |  |  |  | 81.5857 | %
[28 empty] | 79.31% |  |  |  |  | 79.5%
LEV-500-270, pituus 350 mm, s=2 mm
Tulko | 7 | 50%RH
Tpoisto | 20 | 50%RH | [18 empty] | USANON LASKENTA
[21 empty] | Tuloilmapuhallin |  |  | Lämpötilat |  |  |  |  | Lämpötilahyötysuhteet
qV | n, tulo | [19 empty] | Tilavuusvirta | Paine-ero | Hyötysuhde | Ulkoilma | Tuloilma | Poistoilma | Jäteilma | Lämpötilan nousu puhaltimessa | LTO-kennon tuloilman lämpötila-hyötysuhde | Koneen tuloilman lämpötila-hyötysuhde | Koneen tuloilman lämpötilahyötysuhde puhaltimen sähkötehosta puolet huomioiden
120 | 79.1% | [19 empty] | 50 | 89.8756 | 30% | -26 | 11.365 | 21 | -16.365 | 0.24965 | 83.5% | 79.5% | 79.5% | 79.5
100 | 79.7% | [19 empty] | 100 | 159.5023 | 35% | -26 | 11.365 | 21 | -16.365 | 0.37977 | 81.5% | 79.5% | 79.5% | 79.5
90 | 80.1% | [19 empty] | 150 | 246.3801 | 40% | -26 | 11.365 | 21 | -16.365 | 0.51329 | 80.2% | 79.5% | 79.5% | 79.5
70 | 81.3% | [19 empty] | 200 | 349.1202 | 40% | -26 | 10.895 | 21 | -16.365 | 0.72733 | 78.5% | 78.5% | 79.27% | 79.2738
60 | 82.1% | [19 empty] | 250 | 467.3753 | 40% | -26 | 10.284 | 21 | -16.365 | 0.9737 | 77.2% | 77.2% | 78.24% | 78.2358
50 | 83.1% | [19 empty] | 300 | 601.0204 | 40% | -26 | 9.814 | 21 | -16.365 | 1.2521 | 76.2% | 76.2% | 77.53% | 77.532
40 | 84.3% | [19 empty] | 350 | 750 | 40% | -26 | 9.532 | 21 | -16.365 | 1.5625 | 75.6% | 75.6% | 77.26% | 77.2622
30 | 85.9%
25 | 87%
1.0827e-09 | -3.8382e-07 | 5.5261e-05 | -0.0042806 | 0.94769
qV, tulo | 0
qV, poisto | 0
qV, mitoitus | 0
n, tulo, mitoitus | 85%
Airfi model 150
LEV-455-230, pituus 350 mm, s=2.3 mm
Tulko | 7 | 50%RH
Tpoisto | 20 | 50%RH
qV | n, tulo
100
90
80
70
60
50
40
30
22
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
qV, tulo | 0
qV, poisto | 0
qV, mitoitus | 0
n, tulo, mitoitus | #VALUE!

## Laskenta tulopuoli C5 (hidden)
| Tuloilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste | [5 empty] | ÄÄNI | [35 empty] | ILMAN PATTERIA |  |  |  | Suodattimen painehäviöt
[8 empty] | 125 | l/s | 125 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten | [11 empty] | SFPINT -LASKENTA |  |  |  | Puhaltimen paine-eron laskenta | [8 empty] | 10V | -0.00183 | -0.73638 | 1263.0869
| y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V | [18 empty] | 8V | -0.0017835 | -0.36812 | 818.3729 | Suodattimia kolme vaihtoehtoehtoa, hienoin (F8), keskimmäinen (F7) ja karkein (M5) | [9 empty] | ePM 85% F8
| x = til.virta | [12 empty] | 21.0314 | -55.8105 | Ulko |  |  | ----> | Ulko | 45.7359 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  |  |  |  | Suodatinkorjaus | 0 | Korjaus, jos valittu M5 |  | Eri komponenttien painehäviöt | [8 empty] | 6V | -0.0018409 | -0.27749 | 436.4338 | Mitattu tulopuoli keskimmäisellä (F7) | [9 empty] | ePM 65% F7
| 10V | [12 empty] | 23.4191 | -53.4463 | Tulo |  |  | ----> | Tulo | 59.6283 | dB |  |  | 25 | 615.8098 | 20 | 541.1654 | 10 | 383.0095 | 10 | 227.8208 |  |  |  |  | Tuloilman lämpötilahyötysuhde | 80.45% | EN 308 @ qnom |  | Suodatin | Potenssi | 0.071464 | 1.1102 | [5 empty] | 4V | -0.0014239 | -0.39964 | 202.1729 | [10 empty] | ePM10 50% M5
| 2. aste polynomi | [12 empty] | TILAVUUSVIRTA | [10 empty] | 100 | 591.8867 | 50 | 528.9495 | 50 | 360.8293 | 20 | 219.2911 |  |  |  |  | LTO-kojeen nimellisilmavirta (qnom) | 550 |  |  | Kenno | 2. aste | 0.00059822 | 0.059692 | 28.5597 |  |  |  |  | PATTERIN KANSSA |  |  |  | ePM 85% F8 |  |  | ePM 65% F7 |  |  | ePM10 50% M5
| A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos | [6 empty] | 200 | 558.8493 | 100 | 508.0684 | 90 | 337.5265 | 40 | 201.6434 |  |  |  |  | Tulopuhaltimen paine-ero | 193.296 | Pa |  | Muu reitti | Potenssi | 0.00049397 | 2 | [5 empty] | 10V | -0.00183 | -0.73638 | 1263.0869 | qV korj | Pd |  | qV korj | Pd |  | qV korj | Pd
| -0.001899 | -0.84161 | 1263.4182 | [10 empty] | 4-8V | 35.8439 | -22.1908 |  | 4.1064 | ---> | Tulopuhallin | 4.1064 | V | OK |  | 300 | 524.3502 | 150 | 486.4778 | 130 | 312.9113 | 60 | 183.1124 |  |  |  |  | Poistopuhaltimen paine-ero | 167.5761 | Pa | [10 empty] | 8V | -0.0017835 | -0.36812 | 818.3729 | 616.1984 | 144.333 |  | 92.716 | 11.728 |  | 147.3729 | 5.568
[14 empty] | 8V - 10V | 23.1882 | 85.3834 |  | 1.7085 |  |  | TRUE |  |  |  | 400 | 488.1761 | 230 | 450.2577 | 170 | 286.7334 | 160 | 69.7881 | [8 empty] | Suodatin | 15.2094 | Pa | [6 empty] | 6V | -0.0018409 | -0.27749 | 436.4338 | 589.8133 | 138.117 |  | 153.8437 | 19.863 |  | 238.1686 | 9.878
| 8V | [12 empty] | Kaikki 2. x = l/s, y = Vohj | 3.3562e-05 | 0.015042 | 1.7256 | 4.1302 |  | Minimi qV | 100 | l/s |  |  | 500 | 450.0566 | 320 | 406.5835 | 320 | 166.5933 | [6 empty] | Tulopuhaltimen hyötysuhde | 36.81% |  |  | Kenno | 45.3684 | Pa | [6 empty] | 4V | -0.0014239 | -0.39964 | 202.1729 | 398.2311 | 82.931 |  | 253.4274 | 34.451 |  | 349.7764 | 16.643
| 2. aste polynomi | [12 empty] | TEHO | [10 empty] | 520 | 442.17 | 510 | 299.9803 | [8 empty] | Poistopuhaltimen hyötysuhde | 36.01% |  |  | Muu reitti | 7.7183 | Pa | [10 empty] | 279.7502 | 53.301 |  | 324.4671 | 44.194 |  | 409.0469 | 20.115
| A | B | C | [10 empty] | Polynomisovite teholle |  |  |  |  | ----> | Tulopuhallin | 65.645 | W | max | [26 empty] | Onko patteri? |  |  |  | 152.4423 | 25.874 |  | 388.8815 | 54.28 |  | 498.821 | 26.438
| -0.0018526 | -0.47334 | 818.7042 | [9 empty] | 2.aste | 0.012946 | -2.3903 | 166.7331 |  |  |  | Rajoitus | 65.645 | W | 725 | W | [12 empty] | SFP_int_limit | 1241 |  |  | Puhallin | 193.296 | Pa | [6 empty] | TRUE | [6 empty] | 435.0317 | 61.195
[13 empty] | 3.aste | 2.0214e-05 | -0.00036275 | 0.35795 | -8.6923 | [39 empty] | 483.2924 | 69.117
| 6V | [18 empty] | Poistopuhallin | 58.1749 | [15 empty] | SFP_int_tulo | 185.5512 | [11 empty] | Valinta | [6 empty] | 528.5569 | 77.183
| 2. aste polynomi | [11 empty] | 2.aste | 70.226 | W |  |  |  |  | Elektroniikka | 4.4 | W (huom. oli mukana mittaustuloksissa) | [14 empty] | SFP_int_poisto | 118.2441 | [11 empty] | 10V | -0.00183 | -0.73638 | 1263.0869 |  |  |  | 551.9147 | 81.074
| A | B | C | [9 empty] | 3.aste | 69.864 | W | [21 empty] | SFP_int_KOK | 303.7953 | [11 empty] | 8V | -0.0017835 | -0.36812 | 818.3729 | y = AxB
| -0.0019099 | -0.38271 | 436.765 | [9 empty] | KA | 70.045 | W |  |  |  |  | Total power | 128.2199 | W | [18 empty] | Suodatinvaihtoehdot | [8 empty] | 6V | -0.0018409 | -0.27749 | 436.4338 | A | B |  | A | B |  | A | B
[14 empty] | 65.645 | W vähennetty idle | [25 empty] | ISO ePM10 50% (M5) | [8 empty] | 4V | -0.0014239 | -0.39964 | 202.1729 | 0.050776 | 1.2376 | -2.9803 | 0.085933 | 1.0825 | -2.4542 | 0.0092006 | 1.2798 | -4.6885
| 4V | [18 empty] | Maks qV | 125 | l/s | [18 empty] | ISO ePM1 65% (F7) |  |  | 0.071464 | 1.1102
| 2. aste polynomi | [11 empty] | Validointipiste | [6 empty] | SFP | 1.0258 | kW/m3/s | [18 empty] | ISO ePM1 85% (F8/F9) | [12 empty] | Toimintapiste:
| A | B | C | [9 empty] | 165 | l/s | [39 empty] | 125 | l/s
| -0.0014929 | -0.50486 | 202.5042 | [9 empty] | 198 | Pa
Verkkokäyrän potenssikäyrän termi (y=ax^2 --> a = y/x^2)
alfa
0.008
Valintaohjelmassa valittu suodatin
[19 empty] | Verkkokäyrä mitoituspisteelle | [19 empty] | Tehostusvara | [14 empty] | ePM10 50% M5
[19 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Paine puhaltimen yli | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos
[19 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  |  |  |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella |  |  |  | 2-8V | 35.8439 | -22.1908 |  | 4.2808 |  |  |  |  | F8 | F7 | M5 |  | Muutos
[19 empty] | 10 | -0.001899 | -0.84161 | 1263.4182 | -0.009899 | -402.2841 | 317.265 | 615.8098 | 317.265 | 805.2565 | 713.8905 | 66.3759 | 81.329 |  | 10 | 317.265 |  | 0 | Pa |  | 153.8% |  |  | TRUE | (OK, jos TOSI) |  |  | 8V - 10V | 23.1882 | 85.3834 |  | 1.978 |  |  |  | l/s | Pa | Pa | Pa |  | F8 | M5
[19 empty] | 8 | -0.0018526 | -0.47334 | 818.7042 | -0.0098526 | -313.2831 | 265.2406 | 541.1654 | 265.2406 | 562.8205 | 437.9294 | 61.3875 | 77.9225 |  | 8.5 | 282.4827 |  | 0 | Pa |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite |  |  |  | Kaikki 2. x = l/s, y = Vohj | 3.3562e-05 | 0.015042 | 1.7256 | 4.278 |  |  |  | 50 | 6.4317 | 5.9344 | 1.3747 |  | 0.49729 | -4.5598
[19 empty] | 6 | -0.0019099 | -0.38271 | 436.765 | -0.0099099 | -230.1325 | 191.5132 | 383.0095 | 191.5132 | 293.4185 | 188.5418 | 52.7784 | 68.6956 |  | 8 | 265.2406 |  | 0 | Pa |  | 131.25 | l/s |  | 4.2808 | V | [10 empty] | 100 | 15.1665 | 12.5678 | 3.3378 |  | 2.5987 | -9.23
[19 empty] | 4 | -0.0014929 | -0.50486 | 202.5042 | -0.0094929 | -175.0471 | 121.8648 | 227.8208 | 121.8648 | 118.8082 | 66.1256 | 46.252 | 59.3946 |  | 6 | 191.5132 |  | 0 | Pa |  | 137.8125 | Pa | [13 empty] | 150 | 25.0507 | 19.4933 | 5.6082 |  | 5.5573 | -13.8851
[33 empty] | 4 | 121.8648 | [19 empty] | 200 | 35.7639 | 26.6157 | 8.1045 |  | 9.1482 | -18.5113
[54 empty] | 300 | 59.0716 | 41.2825 | 13.6173 |  | 17.7891 | -27.6652
[19 empty] | Spektrikorjaukset |  | Lwokt = LwA + K | [32 empty] | 400 | 84.3344 | 56.3662 | 19.6784 |  | 27.9682 | -36.6878
[54 empty] | 500 | 111.1583 | 71.7676 | 26.1828 |  | 39.3907 | -45.5848
[21 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot | [14 empty] | 600 | 139.2957 | 87.4271 | 33.0639 |  | 51.8686 | -54.3632
[19 empty] | Ulkokanava |  | 11 | 13 | 1 | -4 | -11 | -20 | -23 | -24 | ---> | 56.7359 | 58.7359 | 46.7359 | 41.7359 | 34.7359 | 25.7359 | 22.7359 | 21.7359 | 61.0885 | 45.6761 | OK
[19 empty] | Tulokanava |  | 8 | 8 | 1 | -5 | -5 | -9 | -17 | -24 | ----> | 67.6283 | 67.6283 | 60.6283 | 54.6283 | 54.6283 | 50.6283 | 42.6283 | 35.6283 | 71.2898 | 59.6523 | OK | [18 empty] | F8 | 7.96e-05 | 0.043082 | -2.3369
[54 empty] | Puhallinkäyrät: |  |  |  |  | M5 |  | -0.090615 | -0.25899
[30 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Alkuperäinen suodatin (F7)
[55 empty] | A | B | C
[21 empty] | Tehon sovitteet 2. aste polynomi | [32 empty] | 10 V | -0.00183 | -0.73638 | 1263.0869
[22 empty] | A | B | C | [29 empty] | 8 V | -0.0017835 | -0.36812 | 818.3729 | [6 empty] | Tarkastuksia
[21 empty] | 10V | -0.0011119 | 1.0177 | 502.9315 | [29 empty] | 6 V | -0.0018409 | -0.27749 | 436.4338 | [7 empty] | Mittaus F7 | Hieno F8, lask | Erotus | F8 suodatin | Tarkistus
[21 empty] | 8 V | -0.00083628 | 0.91234 | 254.7746 | [29 empty] | 4 V | -0.0014239 | -0.39964 | 202.1729 | [6 empty] | 100 | 763.7254 | 766.4926 | 2.7672 | 2.7672 | 2.2204e-14 | OK
[21 empty] | 6 V | -0.00065884 | 0.53391 | 110.4558 | [39 empty] | 200 | 673.4071 | 682.8705 | 9.4634 | 9.4634 | 5.1514e-14 | OK
[21 empty] | 4 V | -0.00031655 | 0.2039 | 45.979 | [29 empty] | Hieno suodatin F8 | [9 empty] | 300 | 547.418 | 565.1696 | 17.7515 | 17.7515 | 0 | OK
[55 empty] | A | B | C | [6 empty] | 400 | 385.7582 | 413.3899 | 27.6317 | 27.6317 | 7.816e-14 | OK
| Mitatut pisteet | [52 empty] | 10 V | -0.0017504 | -0.6933 | 1260.75 | [6 empty] | 500 | 188.4276 | 227.5315 | 39.1038 | 39.1038 | 7.816e-14 | OK
| Ulkokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta | [32 empty] | 8 V | -0.0017039 | -0.32504 | 816.036
|  | l/s | LwA | P |  | Sovitteet 2. ja 1. aste ja logaritmi | [5 empty] | l/s | LwA | P |  | Sovitteet 2. ja 1. aste ja logaritmi | [5 empty] | l/s | W | [30 empty] | 6 V | -0.0017613 | -0.23441 | 434.0968
| 10V | 611.2479 | 56.0393 | 717.6345 |  | A | B |  | LwA lask. |  | 10V | 629.1777 | 75.4623 | 721.9422 |  | A | B | C | LwA lask |  | 10V | 110.1892 | 595.9376 | [30 empty] | 4 V | -0.0013443 | -0.35655 | 199.836
|  | 541.6248 | 55.0326 | 710.9436 | 2.aste | 0.0002063 | -0.23041 | 119.662 | 67.3262 |  |  | 532.6579 | 75.545 | 709.5923 | 2.aste | 0.00010659 | -0.12343 | 110.9557 | 82.5243 |  |  | 136.4341 | 615.305
|  | 461.5218 | 57.5552 | 712.2821 | Lin. | -0.03129 | 73.475 |  | 63.5478 |  |  | 450.0813 | 76.9023 | 714.9603 | Lineaarinen | -0.019323 | 86.6778 |  | 80.5471 |  |  | 244.3458 | 686.5624 | [30 empty] | Karkea suodatin M5
|  | 357.6781 | 63.567 | 712.2243 | Log | -15.2535 | 152.3314 |  | 64.4752 |  |  | 348.2313 | 80.9248 | 717.2112 | Log | -9.5129 | 135.9141 |  | 81.1223 |  |  | 287.9238 | 731.1224 | [31 empty] | A | B | C
[22 empty] | 325.0006 | 725.5864 | [30 empty] | 10 V | -0.00183 | -0.827 | 1262.8279
| 8V | 542.1797 | 55.4087 | 496.84 |  | A | B |  |  |  | 8V | 549.8036 | 72.7538 | 498.3194 |  | A | B | C |  |  |  | 367.677 | 725.453 | [30 empty] | 8 V | -0.0017835 | -0.45874 | 818.1139
|  | 472.4746 | 54.4756 | 495.8666 | 2.aste | 0.00017215 | -0.16292 | 93.106 | 62.003 |  |  | 468.9663 | 72.7147 | 496.5432 | 2.aste | 9.4493e-05 | -0.097968 | 98.0082 | 78.671 |  |  | 422.4003 | 715.6693 | [30 empty] | 6 V | -0.0018409 | -0.36811 | 436.1748
|  | 389.7406 | 55.8265 | 482.1274 | Lin. | -0.019606 | 64.7796 |  | 59.5794 |  |  | 390.4772 | 74.2799 | 481.381 | Lineaarinen | -0.018999 | 82.3953 |  | 77.356 |  |  | 458.5544 | 725.9292 | [30 empty] | 4 V | -0.0014239 | -0.49025 | 201.914
|  | 292.9894 | 60.129 | 448.3938 | Log | -8.323 | 106.6043 |  | 60.1567 |  |  | 288.5233 | 77.577 | 442.3959 | Log | -7.9114 | 121.9823 |  | 77.8315 |  |  | 502.5198 | 726.0132
[22 empty] | 538.9994 | 723.1026 | [30 empty] | Valinta | 3
| 6V | 387.6382 | 48.0685 | 227.4727 |  | A | B | C |  |  | 6V | 395.545 | 67.7338 | 219.3543 |  | A | B | C |  |  |  | 576.2267 | 725.5132
|  | 335.5338 | 46.9227 | 227.8725 | 2.aste | 0.00031514 | -0.2081 | 81.3513 | 53.0552 |  |  | 345.8848 | 66.3249 | 221.9346 | 2.aste | 0.00012203 | -0.080336 | 80.1588 | 69.2491 |  |  | 616.0244 | 718.7536 | [30 empty] | Valittu puhallinkäyrä
|  | 277.6444 | 47.9307 | 212.1972 | Lin. | -0.026939 | 57.0228 |  | 51.8636 |  |  | 286.0848 | 67.6823 | 214.2161 | Lineaarinen | -0.0069863 | 69.7396 |  | 68.4016 | [34 empty] | 10 V | -0.00183 | -0.827 | 1262.8279
|  | 191.3716 | 53.0529 | 206.2918 | Log | -7.8977 | 93.7268 |  | 52.2249 |  |  | 208.4663 | 68.5825 | 192.977 | Log | -2.1858 | 80.0523 |  | 68.5659 |  |  | l/s | W | [30 empty] | 8 V | -0.0017835 | -0.45874 | 818.1139
[21 empty] | 8 V | 92.716 | 334.3241 | [30 empty] | 6 V | -0.0018409 | -0.36811 | 436.1748
| 4V | 241.5477 | 39.8325 | 77.1225 |  | A | B | C |  |  | 4V | 245.9501 | 56.0643 | 77.2604 |  | A | B | C |  |  |  | 153.8437 | 372.636 | [30 empty] | 4 V | -0.0014239 | -0.49025 | 201.914
|  | 210.3926 | 38.9078 | 76.5181 | 2.aste | 0.00057318 | -0.2671 | 70.5841 | 46.5463 |  |  | 212.4939 | 55.8486 | 73.4833 |  | 0.00028009 | -0.13424 | 72.0306 | 59.8308 |  |  | 253.4274 | 430.7226
|  | 175.3288 | 42.0961 | 73.1239 | Lin. | -0.053981 | 51.7416 |  | 45.1632 |  |  | 178.2532 | 57.2661 | 71.4181 | Lineaarinen | -0.028288 | 62.4981 |  | 59.0508 |  |  | 324.4671 | 464.7357
|  | 131.6236 | 45.1639 | 68.1621 | Log | -9.966 | 93.5292 |  | 45.6634 |  |  | 133.6705 | 59.0215 | 66.4403 | Log | -5.3109 | 84.856 |  | 59.3484 |  |  | 388.8815 | 482.6274
[22 empty] | 435.0317 | 495.343 | [30 empty] | Lämmitys- ja jäähdytyspatterien vaikutukset
[22 empty] | 483.2924 | 499.7302
| Toimintapisteen tarkistus: | [20 empty] | 528.5569 | 503.1797 | [30 empty] | LÄM-1 | Mittauksissa |  | LÄM-2 | Ei mittauksissa |  | JÄ-1 | Ei mittauksissa |  | JÄ-2 | Ei mittauksissa
[22 empty] | 551.9147 | 503.0499 | [30 empty] | y = AxB |  |  | y = AxB |  |  | y = AxB |  |  | y = AxB
| Onko ohjausjännite alle 10 V |  |  |  |  | TRUE | [47 empty] | A | B |  | A | B |  | A | B |  | A | B
| Onko ohjausjännite yli 2 V |  |  |  |  | TRUE | [15 empty] | l/s | W | [30 empty] | 55.0293 | 1.6981 |  | 84.104 | 1.6735 |  | 79.1979 | 1.718 |  | 104.938 | 1.7095
| Onko paine alle 500 Pa |  |  |  |  | TRUE | [14 empty] | 6V | 386.4773 | 218.0559
| Onko tilavuusvirta alle 10 V verkkokäyrän |  |  |  |  | TRUE | [15 empty] | 355.9054 | 217.6428 | [42 empty] | Kokonaismuutos valituilla pattereilla
| Onko tilavuusvirta yli minimitilavuusvirran? |  |  |  |  | TRUE | [15 empty] | 292.8673 | 210.0567 | [36 empty] | Muutos mitattuun konstruktioon
[22 empty] | 201.6819 | 191.0536 | [31 empty] | LÄM-1 | LÄM-2 | JÄ-1 | JÄ-2 |  | Ei patteria | LÄM-1 | LÄM-2 | Ei patteria | JÄ-1 | JÄ-2 | LÄMM | JÄÄHD | TOT
| Kaikki kunnossa? |  |  |  |  | TRUE | [15 empty] | 93.2383 | 155.4569 | [30 empty] | 50 | 0.33987 | 0.55911 | 0.46086 | 0.62631 |  | -0.33987 | 0 | 0.21925 | 0 | 0.46086 | 0.62631 | 0 | 0.46086 | 0.46086
[22 empty] | 68.6045 | 143.2886 | [30 empty] | 100 | 1.1028 | 1.7835 | 1.5161 | 2.0484 |  | -1.1028 | 0 | 0.68076 | 0 | 1.5161 | 2.0484 | 0 | 1.5161 | 1.5161
| Vanha tarkastus |  |  |  |  | TRUE | [47 empty] | 150 | 2.1954 | 3.5154 | 3.0427 | 4.0967 |  | -2.1954 | 0 | 1.32 | 0 | 3.0427 | 4.0967 | 0 | 3.0427 | 3.0427
[22 empty] | l/s | W | [30 empty] | 200 | 3.5782 | 5.6894 | 4.9877 | 6.6992 |  | -3.5782 | 0 | 2.1112 | 0 | 4.9877 | 6.6992 | 0 | 4.9877 | 4.9877
[21 empty] | 4V | 53.2923 | 55.9714 | [30 empty] | 300 | 7.1235 | 11.214 | 10.0097 | 13.3986 |  | -7.1235 | 0 | 4.0906 | 0 | 10.0097 | 13.3986 | 0 | 10.0097 | 10.0097
[22 empty] | 104.2165 | 63.7238 | [30 empty] | 400 | 11.6105 | 18.1489 | 16.4082 | 21.9101 |  | -11.6105 | 0 | 6.5384 | 0 | 16.4082 | 21.9101 | 0 | 16.4082 | 16.4082
| Spektrikorjaukset (verkkokäyrän mukaan valinta) | [20 empty] | 167.541 | 71.322 | [30 empty] | 500 | 16.9595 | 26.3653 | 24.0741 | 32.0859 |  | -16.9595 | 0 | 9.4058 | 0 | 24.0741 | 32.0859 | 0 | 24.0741 | 24.0741
[22 empty] | 216.8464 | 75.2816 | [30 empty] | 600 | 23.1138 | 35.7722 | 32.9293 | 43.8204 |  | -23.1138 | 0 | 12.6584 | 0 | 32.9293 | 43.8204 | 0 | 32.9293 | 32.9293
Ulkokanava
| Vohj | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | Tarkistus
| 10 | 12 | 6 | 4 | -3 | -8 | -12 | -16 | -22 |  | 0.0023839 | [42 empty] | Valitut patterit
| 8 | 10 | 5 | 4 | -1 | -10 | -14 | -19 | -24 |  | -0.00017693 | [42 empty] | Lämmitys | 3 |  | LÄM-1
| 6 | 11 | 9 | 3 | -1 | -9 | -14 | -20 | -23 |  | 0.31671 | [42 empty] | Jäähdytys | 2 |  | JÄ-1 | FALSE
| 5 | 11 | 11 | 2 | -2.5 | -10 | -17 | -21.5 | -23.5 |  | -0.15094
| 4 | 11 | 13 | 1 | -4 | -11 | -20 | -23 | -24 |  | -0.059823
Muutos mitattuun konstruktioon
Mitoitus | 4.1064 | [53 empty] | 2. asteen sovite, kertoimet
Lähin | 4 | 11 | 13 | 1 | -4 | -11 | -20 | -23 | -24 | [44 empty] | Patterit | 6.9044e-05 | 0.014606 | -0.59026
Tulokanava
| Vohj | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | Tarkistus | [42 empty] | Korjatut puhallinkäyrät (sis. Suodatinvalinta ja patterivalinta)
| 10 | 0 | -5 | 2 | -5 | -7 | -7 | -13 | -13 |  | -0.24639 | [42 empty] | 10 V | -0.001899 | -0.84161 | 1263.4182
| 8 | 0 | -4 | 4 | -4 | -7 | -8 | -14 | -14 |  | 0.16587 | [42 empty] | 8 V | -0.0018526 | -0.47334 | 818.7042
| 6 | 2 | 2 | 4 | -6 | -6 | -8 | -15 | -14 |  | 0.17243 | [42 empty] | 6 V | -0.0019099 | -0.38271 | 436.765
| 5 | 5 | 5 | 2.5 | -5.5 | -5.5 | -8.5 | -16 | -19 |  | -0.10987 | [42 empty] | 4 V | -0.0014929 | -0.50486 | 202.5042
| 4 | 8 | 8 | 1 | -5 | -5 | -9 | -17 | -24 |  | 0.024033
Mitoitus | 4.1064
Lähin | 4 | 8 | 8 | 1 | -5 | -5 | -9 | -17 | -24

## Laskenta poistopuoli C5 (hidden)
| Poistoilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste | [5 empty] | ÄÄNI | [36 empty] | Suodattimen painehäviöt
[8 empty] | 125 | l/s | 125 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten | [15 empty] | Puhaltimen paine-eron laskenta
| y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V | [19 empty] | Suodattimia kolme vaihtoehtoehtoa, hienoin (F8), keskimmäinen (F7) ja karkein (M5) | [8 empty] | ePM 85% F8
| x = til.virta | [12 empty] | 20.6557 | -52.627 | Poisto |  |  | ----> | Poisto | 47.1053 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | [8 empty] | Eri komponenttien painehäviöt | [9 empty] | Mitattu tulopuoli keskimmäisellä (F7) | [8 empty] | ePM 65% F7
| 10V | [12 empty] | 25.6299 | -65.5241 | Jäte |  |  | ----> | Jäte | 58.2251 | dB |  |  | 25 | 704.4152 | 20 | 635.1311 | 10 | 461.4662 | 10 | 281.0751 | [8 empty] | Suodatin | Potenssi | 0.0058255 | 1.433 | [15 empty] | ePM10 50% M5
| 2. aste polynomi | [12 empty] | TILAVUUSVIRTA | [10 empty] | 100 | 672.6394 | 50 | 621.1372 | 50 | 436.2265 | 20 | 271.669 | [8 empty] | Kenno | 2. aste | 0.00030953 | 0.24578 | -5.8216 | [5 empty] | ePM 85% F8 |  |  | ePM 65% F7 |  |  | ePM10 50% M5
| A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos | [6 empty] | 200 | 629.3306 | 100 | 597.2455 | 90 | 409.7502 | 40 | 252.0807 | [8 empty] | Muu reitti | Potenssi | 0.00044457 | 2 | [6 empty] | qV korj | Pd |  | qV korj | Pd |  | qV korj | Pd
| -0.00068301 | -1.4197 | 1363.9982 | [10 empty] | 3-9V | 36.7071 | -15.6187 |  | 3.8308 | ---> | Poistopuhallin | 3.8308 | V | OK |  | 300 | 584.8675 | 150 | 572.5831 | 130 | 381.8354 | 60 | 231.2983 | [18 empty] | 616.1984 | 144.333 |  | 92.716 | 11.728 |  | 147.3729 | 5.568
[14 empty] | 9V - 10V | 17.6945 | 145.9881 |  | -1.1861 |  |  | TRUE |  |  |  | 400 | 539.1524 | 170 | 562.485 | 170 | 352.2185 | 160 | 95.1047 | [8 empty] | Suodatin | 5.8925 | Pa | [7 empty] | 589.8133 | 138.117 |  | 153.8437 | 19.863 |  | 238.1686 | 9.878
| 8V | [12 empty] | Kaikki 2. x = l/s, y = Vohj | 4.9202e-05 | 0.0081837 | 2.1229 | 3.9147 |  | Minimi qV | 100 | l/s |  |  | 500 | 492.0732 | 190 | 552.2452 | 330 | 206.7626 | [10 empty] | Kenno | 29.7371 | Pa | [7 empty] | 398.2311 | 82.931 |  | 253.4274 | 34.451 |  | 349.7764 | 16.643
| 2. aste polynomi | [12 empty] | TEHO | [10 empty] | 530 | 477.6646 | 510 | 362.1499 | [12 empty] | Muu reitti | 6.9464 | Pa | [7 empty] | 279.7502 | 53.301 |  | 324.4671 | 44.194 |  | 409.0469 | 20.115
| A | B | C | [10 empty] | Polynomisovite teholle |  |  |  |  | ----> | Poistopuhallin | 58.1749 | W | max | [27 empty] | 152.4423 | 25.874 |  | 388.8815 | 54.28 |  | 498.821 | 26.438
| -0.0013468 | -0.45187 | 850.2798 | [9 empty] | 2.aste | 0.01412 | -3.0023 | 220.9782 |  |  |  | Rajoitus huomioitu | 58.1749 | W | 725 | W | [16 empty] | Puhallin | 167.5761 | Pa | [10 empty] | 435.0317 | 61.195
[13 empty] | 3.aste | 3.7267e-05 | -0.011239 | 2.4451 | -143.978 | [36 empty] | 483.2924 | 69.117
| 6V | [52 empty] | 528.5569 | 77.183
| 2. aste polynomi | [11 empty] | 2.aste | 66.3123 | W | [38 empty] | 551.9147 | 81.074
| A | B | C | [9 empty] | 3.aste | 58.8375 | W | [35 empty] | y = AxB
| -0.0014314 | -0.29989 | 453.1974 | [9 empty] | KA | 62.5749 | W | [35 empty] | A | B |  | A | B |  | A | B
[14 empty] | 58.1749 | W vähennetty idel | [35 empty] | 0.050776 | 1.2376 | -2.9803 | 0.085933 | 1.0825 | -2.4542 | 0.0092006 | 1.2798 | -4.6885
4V
| 2. aste polynomi | [49 empty] | Toimintapiste:
| A | B | C | [47 empty] | 125 | l/s
| -0.0014531 | -0.25995 | 197.8656
Verkkokäyrän potenssikäyrän termi (y=ax^2 --> a = y/x^2)
alfa
0.008
Valintaohjelmassa valittu suodatin
[19 empty] | Verkkokäyrä mitoituspisteelle | [19 empty] | Tehostusvara | [11 empty] | ePM 85% F8
[19 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Paine puhaltimen yli | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos
[19 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Poisto | Jäte |  | V | l/s |  |  |  |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella |  |  |  | 3-9V | 36.7071 | -15.6187 |  | 4.0011 |  | F8 | F7 | M5 |  | Muutos
[19 empty] | 10 | -0.00068301 | -1.4197 | 1363.9982 | -0.008683 | -486.4411 | 322.9334 | 704.4152 | 322.9334 | 834.288 | 728.5943 | 67.2261 | 81.7565 |  | 10 | 322.9334 |  | 0 | Pa |  | 158.3% |  |  | TRUE | (OK, jos TOSI) |  |  | 9V - 10V | 17.6945 | 145.9881 |  | -0.83292 | l/s | Pa | Pa | Pa |  | F8 | F7
[19 empty] | 8 | -0.0013468 | -0.45187 | 850.2798 | -0.0093468 | -326.7525 | 278.4073 | 635.1311 | 278.4073 | 620.0851 | 469.8058 | 64.259 | 80.0382 |  | 8.5 | 296.3916 |  | 0 | Pa |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite |  |  |  | Kaikki 2. x = l/s, y = Vohj | 4.9202e-05 | 0.0081837 | 2.1229 | 4.0446 | 50 | 6.4317 | 5.9344 | 1.3747 |  | -5.0571 | -4.5598
[19 empty] | 6 | -0.0014314 | -0.29989 | 453.1974 | -0.0094314 | -235.6824 | 203.8854 | 461.4662 | 203.8854 | 332.554 | 203.1926 | 55.1044 | 70.1869 |  | 8 | 278.4073 |  | 0 | Pa |  | 131.25 | l/s |  | 4.0011 | V | [7 empty] | 100 | 15.1665 | 12.5678 | 3.3378 |  | -11.8287 | -9.23
[19 empty] | 4 | -0.0014531 | -0.25995 | 197.8656 | -0.0094531 | -159.0776 | 131.5789 | 281.0751 | 131.5789 | 138.5041 | 68.06 | 49.1426 | 59.6224 |  | 6 | 203.8854 |  | 0 | Pa |  | 137.8125 | Pa | [10 empty] | 150 | 25.0507 | 19.4933 | 5.6082 |  | -19.4424 | -13.8851
[33 empty] | 4 | 131.5789 | [16 empty] | 200 | 35.7639 | 26.6157 | 8.1045 |  | -27.6595 | -18.5113
[51 empty] | 300 | 59.0716 | 41.2825 | 13.6173 |  | -45.4543 | -27.6652
[19 empty] | Spektrikorjaukset |  | Lwokt = LwA + K | [29 empty] | 400 | 84.3344 | 56.3662 | 19.6784 |  | -64.656 | -36.6878
[51 empty] | 500 | 111.1583 | 71.7676 | 26.1828 |  | -84.9755 | -45.5848
[21 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot | [11 empty] | 600 | 139.2957 | 87.4271 | 33.0639 |  | -106.2318 | -54.3632
[19 empty] | Poistokanava |  | 8 | 11 | 3 | -4 | -8 | -16 | -23 | -23 | ---> | 55.1053 | 58.1053 | 50.1053 | 43.1053 | 39.1053 | 31.1053 | 24.1053 | 24.1053 | 60.4269 | 47.0702 | OK
[19 empty] | Jätekanava |  | 6 | 6 | 1 | -4 | -5 | -8 | -17 | -22 | ----> | 64.2251 | 64.2251 | 59.2251 | 54.2251 | 53.2251 | 50.2251 | 41.2251 | 36.2251 | 68.2769 | 58.3398 | OK | [15 empty] | F8 | -7.3374e-05 | -0.13769 | 2.499
[51 empty] | Puhallinkäyrät: |  |  |  |  | M5 |  | -0.090615 | -0.25899
[30 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Alkuperäinen suodatin (M5)
[52 empty] | A | B | C
[21 empty] | Tehon sovitteet 2. aste polynomi | [29 empty] | 10 V | -0.00068301 | -1.4197 | 1363.9982
[22 empty] | A | B | C | [26 empty] | 8 V | -0.0013468 | -0.45187 | 850.2798
[21 empty] | 10V | 0.00013577 | -0.16703 | 768.3758 | [26 empty] | 6 V | -0.0014314 | -0.29989 | 453.1974
[21 empty] | 8 V | -0.00089835 | 0.98686 | 264.6895 | [26 empty] | 4 V | -0.0014531 | -0.25995 | 197.8656
[21 empty] | 6 V | -0.00063128 | 0.53638 | 120.0748
[21 empty] | 4 V | -0.00031327 | 0.19942 | 47.2442 | [26 empty] | Hienoin suodatin F8
[52 empty] | A | B | C
| Mitatut pisteet | [49 empty] | 10 V | -0.00075639 | -1.5574 | 1366.4972
| Poistokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta | [29 empty] | 8 V | -0.0014202 | -0.58956 | 852.7788
|  | l/s | LwA | P |  | Sovitteet 2. ja 1. aste | [5 empty] | l/s | LwA | P |  | 2. aste tai Lineaarinen | [5 empty] | l/s | W | [27 empty] | 6 V | -0.0015047 | -0.43758 | 455.6964
| 10V | 659.7478 | 59.5049 | 714.998 |  | A | B |  | LwA lask. |  | 10V | 678.3754 | 78.8721 | 728.2009 |  | A | B | C | LwA lask |  | 10V | 674.363 | 716.4962 | [27 empty] | 4 V | -0.0015265 | -0.39764 | 200.3646
|  | 568.5265 | 58.804 | 715.4639 | 2.aste | 0.00013068 | -0.15376 | 104.0476 | 68.0209 |  |  | 567.7272 | 77.458 | 727.0865 | 2.aste | 9.9698e-05 | -0.10982 | 107.5317 | 82.4642 |  |  | 619.7562 | 721.2394
|  | 489.9628 | 60.139 | 729.9775 | Lin. | -0.019918 | 71.2798 |  | 64.8476 |  |  | 477.8586 | 77.6821 | 719.5489 | Lineaarinen | -0.0061803 | 81.9467 |  | 79.9509 |  |  | 575.7098 | 711.9259 | [27 empty] | Hieno suodatin F7
|  | 368.7996 | 65.1014 | 719.2175 | Log | -10.3821 | 125.6187 |  | 65.6364 |  |  | 361.893 | 80.8836 | 716.0163 | Log | -3.5695 | 100.9636 |  | 80.3411 |  |  | 531.9102 | 721.6919 | [28 empty] | A | B | C
[22 empty] | 485.8736 | 712.8273 | [27 empty] | 10 V | -0.00068301 | -1.5104 | 1363.7392
| 8V | 593.1876 | 56.951 | 530.9957 |  | A | B |  |  |  | 8V | 609.3295 | 76.6223 | 537.5809 |  | A | B | C |  |  |  | 448.2772 | 727.1308 | [27 empty] | 8 V | -0.0013468 | -0.54249 | 850.0208
|  | 512.479 | 56.5518 | 533.0673 | 2.aste | 7.981e-05 | -0.09423 | 84.5401 | 64.4919 |  |  | 511.4538 | 75.2999 | 534.1655 | 2.aste | 0.00012176 | -0.12027 | 104.7658 | 80.7182 |  |  | 382.2419 | 722.5775 | [27 empty] | 6 V | -0.0014314 | -0.3905 | 452.9384
|  | 440.1528 | 59.0593 | 515.9378 | Lin. | -0.023209 | 69.6615 |  | 63.2 |  |  | 420.1791 | 75.5379 | 512.069 | Lineaarinen | -0.0084326 | 80.5704 |  | 78.2227 |  |  | 332.9889 | 727.9801 | [27 empty] | 4 V | -0.0014531 | -0.35056 | 197.6066
|  | 304.8837 | 63.1311 | 487.822 | Log | -10.1696 | 121.0389 |  | 63.7932 |  |  | 310.6272 | 79.2079 | 489.9651 | Log | -4.2062 | 102.3551 |  | 78.6781 |  |  | 290.3515 | 721.5716
[22 empty] | 253.0926 | 719.4538 | [27 empty] | Valinta | 1
| 4V | 430.3087 | 51.3977 | 245.9717 |  | A | B | C |  |  | 4V | 454.5165 | 70.4817 | 249.2112 |  | A | B | C |  |  |  | 136.291 | 658.1619
|  | 368.9061 | 51.0375 | 241.487 | 2.aste | 0.00010353 | -0.083148 | 67.9117 | 55.2629 |  |  | 386.0851 | 69.141 | 246.1764 | 2.aste | 0.00011214 | -0.074275 | 81.0817 | 70.5996 | [31 empty] | Valittu puhallinkäyrä
|  | 317.3987 | 52.1903 | 242.196 | Lin. | -0.016712 | 57.9012 |  | 54.4938 |  |  | 316.4367 | 68.7891 | 239.0282 | Lineaarinen | 0.0021834 | 68.833 |  | 69.2782 |  |  | l/s | W | [27 empty] | 10 V | -0.00068301 | -1.4197 | 1363.9982
|  | 217.4203 | 54.6847 | 211.8593 | Log | -5.3278 | 83.118 |  | 54.7874 |  |  | 229.4673 | 69.9476 | 223.2775 | Log | 0.45722 | 66.9301 |  | 69.3615 |  | 8 V | 122.2491 | 375.4097 | [27 empty] | 8 V | -0.0013468 | -0.45187 | 850.2798
[22 empty] | 219.8837 | 432.0416 | [27 empty] | 6 V | -0.0014314 | -0.29989 | 453.1974
| 2V | 266.4348 | 42.1996 | 79.715 |  | A | B | C |  |  | 2V | 275.5139 | 58.1229 | 78.1281 |  | A | B | C |  |  |  | 291.3766 | 475.1066 | [27 empty] | 4 V | -0.0014531 | -0.25995 | 197.8656
|  | 233.0427 | 41.8785 | 78.4557 | 2.aste | 0.00048988 | -0.24957 | 73.798 | 49.441 |  |  | 239.4023 | 57.4097 | 79.1608 | 2.aste | 0.00028346 | -0.128 | 71.8533 | 59.9191 |  |  | 373.6152 | 511.296
|  | 205.0479 | 43.5083 | 76.9557 | Lin. | -0.050995 | 54.7158 |  | 48.0059 |  |  | 197.9147 | 57.6629 | 76.3246 | Lineaarinen | -0.0089655 | 60.0224 |  | 58.8428 |  |  | 432.7253 | 523.1169
|  | 143.4285 | 48.0352 | 69.905 | Log | -10.2719 | 98.6684 |  | 48.5457 |  |  | 146.0848 | 59.1936 | 71.7836 | Log | -2.0143 | 68.8582 |  | 59.0291 |  |  | 492.2331 | 534.2333
[22 empty] | 553.3568 | 537.6576
[22 empty] | 608.0627 | 529.8537
Toimintapisteen tarkistus:
[22 empty] | l/s | W
| Onko ohjausjännite alle 10 V |  |  |  |  | TRUE | [14 empty] | 6V | 437.095 | 233.9793
| Onko ohjausjännite yli 2 V |  |  |  |  | TRUE | [15 empty] | 394.2816 | 233.3462
| Onko paine alle 500 Pa |  |  |  |  | TRUE | [15 empty] | 328.648 | 228.0184
| Onko tilavuusvirta alle 10 V verkkokäyrän |  |  |  |  | TRUE | [15 empty] | 239.2669 | 212.6556
| Onko tilavuusvirta yli minimitilavuusvirran? |  |  |  |  | TRUE | [15 empty] | 125.0968 | 176.7355
[22 empty] | 87.5189 | 162.5212
| Kaikki kunnossa? |  |  |  |  | TRUE
[22 empty] | l/s | W
| Vanha tarkastus |  |  |  |  | TRUE | [14 empty] | 4 V | 51.0132 | 56.6605
[22 empty] | 136.0144 | 68.2987
[22 empty] | 183.805 | 73.6009
[22 empty] | 259.6592 | 77.8334
Spektrikorjaukset (verkkokäyrän mukaan valinta)
Poistokanava
| Vohj | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | Tarkistus
| 10 | 8 | 2 | 4 | -3 | -7 | -11 | -15 | -22 |  | -0.045369
| 8 | 7 | 2 | 5 | -2 | -8 | -12 | -16 | -24 |  | 0.27683
| 6 | 6 | 6 | 4 | -2 | -7 | -12 | -18 | -25 |  | 0.25763
| 5 | 7 | 8.5 | 3.5 | -3 | -7.5 | -14 | -20.5 | -24 |  | -0.090688
| 4 | 8 | 11 | 3 | -4 | -8 | -16 | -23 | -23 |  | -0.035161
Mitoitus | 3.8308
Lähin | 4 | 8 | 11 | 3 | -4 | -8 | -16 | -23 | -23
Jätekanava
| Vohj | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | Tarkistus
| 10 | -1 | -5 | 2 | -5 | -6 | -7 | -14 | -14 |  | -0.10979
| 8 | -2 | -4 | 4 | -5 | -7 | -8 | -15 | -15 |  | -0.078034
| 6 | 0 | 1 | 4 | -5 | -6 | -8 | -16 | -15 |  | 0.2023
| 5 | 3 | 3.5 | 2.5 | -4.5 | -5.5 | -8 | -16.5 | -18.5 |  | 0.021454
| 4 | 6 | 6 | 1 | -4 | -5 | -8 | -17 | -22 |  | 0.11475
Mitoitus | 3.8308
Lähin | 4 | 6 | 6 | 1 | -4 | -5 | -8 | -17 | -22

## Laskenta vaipan läpi C5 (hidden)
Verkkokäyrän positio
Ohjausjännite |  |  | Alfa | Keskiarvo Alfa |  |  |  |  | Tulopuoli | [5 empty] | Poistopuoli | [5 empty] | P* [W] | Äänitehotasot oktaavikaistoittain LW,okt [dB] | [7 empty] | LW,kok** [dB] | LW,A,kok** [dB]
Tulo | 4.1064 | V | 0.008 | 0.008 |  |  |  |  | Ohj.-% [%] | Uohj [V] | qV [dm3/s] | ps21 [Pa] | ps22 [Pa] | ptU [Pa] | Ohj.-% [%] | Uohj [V] | qV [dm3/s] | ps11 [Pa] | ps12 [Pa] | ptU [Pa] |  | 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz
Poisto | 3.8308 | V | 0.008
[9 empty] | 100 | 10.013 | 593.4969 | -60.7794 | 113.2158 | 173.9952 | 10 | 9.997 | 637.2837 | -41.769 | 138.7471 | 180.5161 | 1453.9597 | 63.2771 | 57.8009 | 52.1454 | 44.2695 | 42.589 | 42.2014 | 34.8491 | 33.0474 | 64.7127 | 49.9595 | 13.3176 | 7.8414 | 2.1859 | -5.69 | -7.3705 | -7.7581 | -15.1104 | -16.9121
Sovite ohj. Jännite vs. LwA vaipan läpi | [8 empty] | 100 | 9.9979 | 530.7312 | -134.9954 | 198.0536 | 333.049 | 10 | 10.01 | 566.4218 | -146.5733 | 193.3292 | 339.9025 | 1440.1126 | 60.7653 | 56.5165 | 53.0563 | 43.6984 | 42.0978 | 41.8559 | 34.5362 | 33.0934 | 62.7946 | 49.6222 | 11.1432 | 6.8944 | 3.4341 | -5.9238 | -7.5244 | -7.7662 | -15.086 | -16.5288
y = LwA, x = ohjausjännite | [8 empty] | 100 | 9.999 | 444.9321 | -215.6245 | 321.2308 | 536.8553 | 10 | 9.999 | 476.4978 | -202.0453 | 325.0603 | 527.1056 | 1447.0854 | 65.657 | 58.7916 | 57.3928 | 44.975 | 42.0805 | 41.7865 | 34.4157 | 33.2385 | 67.0347 | 51.5729 | 14.0842 | 7.2188 | 5.8199 | -6.5979 | -9.4924 | -9.7864 | -17.1572 | -18.3344
y = Ax + B | [8 empty] | 100 | 10.011 | 356.4799 | -352.6929 | 368.555 | 721.2479 | 10 | 10.013 | 380.2816 | -365.9889 | 358.9452 | 724.9341 | 1430.2612 | 68.6063 | 63.3225 | 62.3346 | 49.0194 | 43.6508 | 42.9907 | 35.9776 | 34.5826 | 70.5098 | 55.3755 | 13.2307 | 7.9469 | 6.9591 | -6.3562 | -11.7247 | -12.3848 | -19.3979 | -20.7929
| A | B | [6 empty] | 80 | 8 | 525.4352 | -46.0793 | 87.2786 | 133.358 | 8 | 8.013 | 574.8086 | -33.3846 | 113.3456 | 146.7302 | 1036.124 | 60.1592 | 55.8451 | 53.0568 | 40.8158 | 40.4872 | 39.4497 | 31.5503 | 30.4206 | 62.1965 | 48.1244 | 12.0348 | 7.7207 | 4.9324 | -7.3086 | -7.6372 | -8.6747 | -16.5741 | -17.7038
Kaikki voltit | 12.7483 | 23.0019 |  | Korjaus, lisätään tulokseen |  |  |  |  | 80 | 7.999 | 461.8448 | -117.649 | 149.2807 | 266.9296 | 8 | 8.0121 | 510.3506 | -119.3748 | 158.1579 | 277.5327 | 1046.5191 | 60.1256 | 57.8395 | 53.8238 | 40.6695 | 39.8639 | 39.0144 | 31.5896 | 29.8743 | 62.8111 | 48.629 | 11.4966 | 9.2105 | 5.1948 | -7.9595 | -8.7651 | -9.6146 | -17.0394 | -18.7548
VK sijainnin korjaus | 992.6163 | -2.648 | 5.2929 | 4 | dB |  |  |  | 80 | 8.0072 | 386.1345 | -163.8424 | 242.107 | 405.9495 | 8 | 7.997 | 417.6378 | -160.3012 | 262.2522 | 422.5534 | 1000.8261 | 60.6423 | 56.9155 | 57.4584 | 41.5267 | 39.7004 | 39.2384 | 31.4939 | 29.8963 | 63.5068 | 49.868 | 10.7743 | 7.0475 | 7.5903 | -8.3414 | -10.1676 | -10.6296 | -18.3742 | -19.9718
[9 empty] | 80 | 8.014 | 281.3086 | -314.1446 | 236.3341 | 550.4788 | 8 | 8.005 | 317.5746 | -284.6807 | 272.2574 | 556.9381 | 940.3741 | 63.6842 | 62.8161 | 62.0251 | 46.7283 | 41.379 | 39.8657 | 33.0714 | 30.8509 | 67.7203 | 54.0112 | 9.673 | 8.8049 | 8.0139 | -7.2828 | -12.6322 | -14.1454 | -20.9398 | -23.1603
|  |  |  | Ilman korjausta |  | Korjauksen kanssa |  |  | 60 | 5.998 | 375.7907 | -26.4112 | 44.9933 | 71.4045 | 6 | 6.002 | 418.2425 | -17.5129 | 60.7191 | 78.232 | 459.097 | 51.9619 | 53.4972 | 48.5773 | 34.9732 | 34.1612 | 32.1811 | 22.3602 | 22.8043 | 56.6338 | 43.0434 | 8.9185 | 10.4537 | 5.5338 | -8.0702 | -8.8822 | -10.8623 | -20.6832 | -20.2391
Maksimi | 4.1064 | V | ---> | 41.0096 | dB | 45.0096 | dB |  | 60 | 6.006 | 328.8163 | -68.7038 | 77.7602 | 146.4641 | 6 | 5.995 | 368.0464 | -66.8942 | 87.5276 | 154.4218 | 460.9892 | 55.4822 | 54.2647 | 50.1807 | 36.4026 | 34.5481 | 32.4633 | 24.3293 | 23.0126 | 58.6572 | 44.2743 | 11.2079 | 9.9904 | 5.9065 | -7.8717 | -9.7262 | -11.8109 | -19.9449 | -21.2617
Painotettu keskiarvo | 4.0146 | V | ---> | 40.7211 | dB | 44.7211 | dB |  | 60 | 5.997 | 285.8014 | -89.4266 | 134.8345 | 224.2611 | 6 | 5.994 | 293.8264 | -90.5814 | 147.8217 | 238.4031 | 455.5234 | 53.5918 | 58.9923 | 50.7896 | 37.6884 | 35.7325 | 34.8768 | 26.2457 | 22.5829 | 60.6251 | 47.2018 | 6.39 | 11.7905 | 3.5878 | -9.5134 | -11.4693 | -12.325 | -20.9561 | -24.6189
[9 empty] | 60 | 6.01 | 205.5732 | -173.2809 | 129.8311 | 303.1119 | 6 | 6.007 | 216.3634 | -159.9105 | 151.9328 | 311.8434 | 418.0616 | 62.8202 | 64.3372 | 52.6435 | 38.1196 | 35.1697 | 33.4597 | 23.3657 | 22.566 | 66.8352 | 51.0677 | 11.7525 | 13.2695 | 1.5758 | -12.9481 | -15.898 | -17.608 | -27.702 | -28.5017
Korjaus | [8 empty] | 40 | 4 | 234.0116 | -9.7088 | 17.277 | 26.9858 | 4 | 3.9969 | 260.9073 | -6.2146 | 23.9395 | 30.1541 | 154.1637 | 54.0425 | 51.11 | 46.0561 | 30.2091 | 26.0447 | 21.5048 | 12.1675 | 15.4162 | 56.2814 | 39.0564 | 14.9861 | 12.0536 | 6.9997 | -8.8473 | -13.0117 | -17.5516 | -26.8889 | -23.6402
[9 empty] | 40 | 3.997 | 203.3281 | -22.3132 | 34.0163 | 56.3295 | 4 | 4 | 235.2757 | -24.0766 | 35.0232 | 59.0997 | 151.2011 | 48.7854 | 52.9874 | 43.9833 | 27.9566 | 23.7805 | 22.3877 | 13.2296 | 14.372 | 54.7807 | 38.7301 | 10.0552 | 14.2573 | 5.2532 | -10.7735 | -14.9496 | -16.3424 | -25.5006 | -24.3581
Äänitehotasot kanaviin | [8 empty] | 40 | 3.994 | 177.0674 | -33.0991 | 52.4347 | 85.5338 | 4 | 3.999 | 189.6746 | -35.5372 | 61.4231 | 96.9603 | 148.4299 | 52.775 | 55.0119 | 44.5739 | 31.6475 | 28.5604 | 26.2659 | 10.9908 | 11.4462 | 57.3066 | 40.2242 | 12.5508 | 14.7877 | 4.3497 | -8.5767 | -11.6638 | -13.9583 | -29.2334 | -28.778
Imupuoli | Ulko | 45.7359 | dB | [5 empty] | 40 | 3.997 | 126.1926 | -72.9575 | 50.9719 | 123.9295 | 4 | 4 | 143.3867 | -65.0136 | 63.2021 | 128.2157 | 137.7368 | 54.0436 | 59.1128 | 44.079 | 34.2881 | 32.1371 | 28.7704 | 19.2528 | 15.1185 | 60.4128 | 42.8259 | 11.2177 | 16.2869 | 1.2531 | -8.5378 | -10.6888 | -14.0556 | -23.5731 | -27.7074
| Poisto | 47.0702 | dB | [6 empty] | V | LwA | alfa T | alfa P | alfa KA |  | LwA lask | Erotus |  | Korjaus | LwA Lask korjattu |  | Erotus korj.
| Erotus | 1.3343 | dB | [6 empty] | 10.013 | 49.9595 | 0.00049397 | 0.00044448 | 0.00046922 |  | 52.3725 | -2.413 |  | -2.1822 | 50.1902 |  | 0.23074 | [9 empty] | 11.4271 | 10.3484 | 4.9119 | -8.1624 | -10.7252 | -12.2046 | -20.8851 | -21.954
[10 empty] | 9.9979 | 49.6222 | 0.0011824 | 0.0010594 | 0.0011209 |  | 52.3532 | -2.7311 |  | -1.5354 | 50.8179 |  | 1.1957 | [9 empty] | 11 | 10 | 5 | -8 | -11 | -12 | -21 | -22
Painepuoli | Tulo | 59.6283 | dB | [6 empty] | 9.999 | 51.5729 | 0.0027119 | 0.0023215 | 0.0025167 |  | 52.3546 | -0.78175 |  | -0.14987 | 52.2048 |  | 0.63188
| Jäte | 58.3398 | dB | [6 empty] | 10.011 | 55.3755 | 0.0056756 | 0.0050129 | 0.0053443 |  | 52.3699 | 3.0056 |  | 2.6568 | 55.0267 |  | -0.3488
| Erotus | 1.2885 | dB | [6 empty] | 8 | 48.1244 | 0.00048304 | 0.00044409 | 0.00046356 |  | 49.5112 | -1.3868 |  | -2.1879 | 47.3234 |  | -0.80101
[10 empty] | 7.999 | 48.629 | 0.0012514 | 0.0010656 | 0.0011585 |  | 49.5096 | -0.88061 |  | -1.4981 | 48.0116 |  | -0.61744
Keskiarvo erotus | 1.3114 | dB | [7 empty] | 8.0072 | 49.868 | 0.0027227 | 0.0024226 | 0.0025726 |  | 49.5227 | 0.34536 |  | -0.094353 | 49.4283 |  | -0.43971
Korjaus K | 2.8397 | dB | [7 empty] | 8.014 | 54.0112 | 0.0069562 | 0.0055222 | 0.0062392 |  | 49.5335 | 4.4777 |  | 3.5452 | 53.0787 |  | -0.93249
[10 empty] | 5.998 | 43.0434 | 0.00050563 | 0.00044723 | 0.00047643 |  | 45.8395 | -2.7961 |  | -2.1751 | 43.6644 |  | 0.62099
Taustamelukorjattu | 47.8493 | dB | [7 empty] | 6.006 | 44.2743 | 0.0013546 | 0.00114 | 0.0012473 |  | 45.8565 | -1.5822 |  | -1.4099 | 44.4466 |  | 0.17235
Maksimikorjaus | 42.4096 | dB | [7 empty] | 5.997 | 47.2018 | 0.0027455 | 0.0027614 | 0.0027535 |  | 45.8374 | 1.3644 |  | 0.085142 | 45.9225 |  | -1.2793
|  |  |  | LpA10m2 | LpA2,5m2 |  |  |  |  | 6.01 | 51.0677 | 0.0071725 | 0.0066614 | 0.006917 |  | 45.865 | 5.2027 |  | 4.2179 | 50.0829 |  | -0.98481
Valinta | 44.7211 | dB |  | 40.7417 | 46.7623 |  |  |  |  | 4 | 39.0564 | 0.00049279 | 0.00044297 | 0.00046788 |  | 40.6748 | -1.6184 |  | -2.1836 | 38.4912 |  | -0.5652
[10 empty] | 3.997 | 38.7301 | 0.0013625 | 0.0010677 | 0.0012151 |  | 40.6652 | -1.9351 |  | -1.4419 | 39.2233 |  | 0.4932
[10 empty] | 3.994 | 40.2242 | 0.0027281 | 0.0026951 | 0.0027116 |  | 40.6556 | -0.43143 |  | 0.043589 | 40.6992 |  | 0.47502
[10 empty] | 3.997 | 42.8259 | 0.0077823 | 0.0062362 | 0.0070093 |  | 40.6652 | 2.1607 |  | 4.3095 | 44.9747 |  | 2.1488
[10 empty] | Logaritmisovite Vohj vs LwA | [8 empty] | Verkkokäyräposition korjaus
[10 empty] | 12.7483 | 23.0019 | [5 empty] | 2.0696 |  | 992.6163 | -2.648 |  | 0.74609 | dB
[19 empty] | Max | Min
[19 empty] | 1 | -1
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 11 | 10 | 5 | -8 | -11 | -12 | -21 | -22 | ---> | 55.7211 | 54.7211 | 49.7211 | 36.7211 | 33.7211 | 32.7211 | 23.7211 | 22.7211 | 58.882 | 44.5689 |  | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta vesipatteri C5 (hidden)
|  |  |  | Syötettävät tiedot |  |  | Reynolds-luvun vaikutus korjattavaan lämpötilaeroon
|  |  |  | Tilavuusvirta | 25 | dm3/s
|  |  |  | Tarvittava teho | 570 | W | Tilavuusvirta | Reynolds | Korjaus lämpötilaeroon
|  |  |  | Patterille tulevan ilman lämpötila | 1 | °C | 50 | 4388.9688 | 0.29667
|  |  |  | Patterilta lähtevän ilman lämpötila | 20 | °C | 50 | 5309.2365 | -0.47043
|  |  |  | Menoveden lämpötila | 50 | °C | 50 | 8494.7784 | 0.72366
|  |  |  | Paluuveden lämpötila | 30 | °C | 50 | 4388.9688 | 0.29667 | Korjaus | 0.3
|  |  |  | Arvio Reynolds-luvusta | 1210.5059 | - | 50 | 3964.2299 | 0.41312
|  |  |  | Tarvittava lämpötilaero patterilla | 6.767 | K | 50 | 3539.491 | -0.47043
[7 empty] | 50 | 3114.7521 | -0.85398
|  |  |  | Patterimitoitus menoveden lämpötilan mukaan |  |  | 100 | 7078.982 | 0.8965
|  |  |  | Menoveden lämpötila | 50 | °C | 100 | 8707.1479 | 0.61513
Virhetilanne |  | TRUE | FALSE | Paluuveden lämpötila | -15.4661 | °C | 100 | 13591.6455 | 0.83376
|  | FALSE |  | Virtaama | 0.00208 | dm3/s | 100 | 3822.6503 | -4.9373 | Korjaus | -4.5
|  | FALSE |  | Painehäviö | 0.010445 | kPa | 100 | 7078.982 | 0.8965
|  | FALSE |  | Painehäviö säätövent (KV=1,00) | 0.0056069 | kPa | 100 | 6512.6635 | 1.1048 | 0.0017873 | -10.939 |  | Korjaus lämpötilaeroon
|  | TRUE |  | Virtausnopeus | 0.016949 | m/s | 100 | 5663.1856 | -0.5828
| VIRHE | TRUE |  | Reynolds | 369.8117 | - | 100 | 4955.2874 | -1.0725 |  |  |  | 0.3
[7 empty] | 200 | 11184.7916 | 1.439
|  |  |  | Patterimitoitus paluuveden lämpötilan mukaan |  |  | 200 | 13804.0149 | 1.3612 |  |  |  | 50 | 0.3
Virhetilanne |  | FALSE | TRUE | Menoveden lämpötila | 4.5339 | °C | 200 | 22511.1628 | 2.7945 |  |  |  | 100 | -4.5
|  | FALSE |  | Paluuveden lämpötila | 30 | °C | 200 | 6158.7144 | -4.3388 | Korjaus | -4.5 |  | 200 | -4.5
|  |  |  | Virtaama | -0.005347 | dm3/s | 200 | 11184.7916 | 1.439 |  |  |  | 300 | -4.5
|  | TRUE |  | Painehäviö | #NUM! | kPa | 200 | 9910.5748 | -0.111 | 0.0011045 | -11.0314
|  | TRUE |  | Painehäviö säätövent (KV=1,00) | 0.037054 | kPa | 200 | 8494.7784 | -2.1666 |  |  |  | -0.014644 | -0.92034
|  | TRUE |  | Virtausnopeus | -0.043572 | m/s | 200 | 7503.7209 | -2.2055
| VIRHE | TRUE |  | Reynolds | -950.6817 | - | 300 | 14299.5437 | 2.5297 |  |  |  | 0.00018332 | -0.079116 | 3.0256
[7 empty] | 300 | 17626.6652 | 2.2719
[7 empty] | 300 | 25909.0742 | -0.20978
[7 empty] | 300 | 7645.3006 | -4.4845 | Korjaus | -4.5
[7 empty] | 300 | 14299.5437 | 2.5297
[7 empty] | 300 | 12175.8491 | -0.93511 | 0.0010014 | -12.3554
[7 empty] | 300 | 10760.0527 | -1.745
[7 empty] | 300 | 9202.6766 | -2.9858
Tarvittavan lämpötilaeron laskenta
[7 empty] | Tilavuusvirta | Kerroin |  | Eksponenttisovite
[7 empty] | 50 | 0.10404 |  | 0.45113 | -4.0233 | 0.017894
[7 empty] | 100 | 0.14328 |  | 0.076448
[7 empty] | 200 | 0.1978
[7 empty] | 300 | 0.23203 |  | 3-asteen polynomin sovite
[10 empty] | 2.331e-09 | -2.4135e-06 | 0.0011061 | 0.054477
0.080657
Nestepuolen painehäviö
[7 empty] | 1.787 | 6.4739 | 648.0329

## Laskenta_vuosihyötysuhde_C (hidden)
| Hakee arvot tulostus-välilehdeltä. |  |  |  | -26 |  | 21 | -6.5 | -6.5 | -6.5 | 21 | 21 | 1.5 |  | 1 | 58.51% | 58.51%
| Älä muuta tästä! | [17 empty] | Total | 4410.75 | 3665.3332 | 3665.3332
| Sisälämpötila | 21 | °C |  | tu | Aika vuodessa | tLTO,maks | tj | tj,min | tj,maks | tj, korjaamaton | tsisä | tLTO | tLTO, korjaamaton | RLTO | ηt | ηp | ηt, korjaamaton | ηp,korjaamaton | SS,Kd | ST,Kd | SJ,Kd
| Tuloilmamäärä | 125 | l/s |  | -32 | 0 | 21 | -6.5 | -6.5 | -6.5 | -23.043 | 21 | -4.5 | 12.043 | 1 | 51.89% | 51.89% | 83.1% | 83.1% | 0 | 0 | 0 | #VALUE! | #VALUE! | Ilmanvaihdon kokonaisenergiantarve |  | 15973.9722 | kWh
| Poistoilmamäärä | 125 | l/s |  | -31 | 0 | 21 | -6.5 | -6.5 | -6.5 | -22.212 | 21 | -3.5 | 12.212 | 1 | 52.88% | 52.88% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0 | Talteenotettu lämmitysenergia |  | 13274.3709 | kWh | Teho (puhaltimet + elektroniikka)
| RLTO | 1 |  |  | -30 | 0 | 21 | -6.5 | -6.5 | -6.5 | -21.381 | 21 | -2.5 | 12.381 | 1 | 53.92% | 53.92% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0 | Ilmanvaihtokoneen energiankulutus |  | 1123.2064 | kWh | 128.2199 | W
| nLTO 1 | 83.1% |  |  | -29 | 0 | 21 | -6.5 | -6.5 | -6.5 | -20.55 | 21 | -1.5 | 12.55 | 1 | 55% | 55% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
| nLTO, RT | 83.1% |  |  | -28 | 0 | 21 | -6.5 | -6.5 | -6.5 | -19.719 | 21 | -0.5 | 12.719 | 1 | 56.12% | 56.12% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
| Minimi jäteilma | -6.5 | °C |  | -27 | 0 | 21 | -6.5 | -6.5 | -6.5 | -18.888 | 21 | 0.5 | 12.888 | 1 | 57.29% | 57.29% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0 | Tavoitelämpötila |  | 21
| Maksimi tLTO | 21 | °C |  | -26 | 0 | 21 | -6.5 | -6.5 | -6.5 | -18.057 | 21 | 1.5 | 13.057 | 1 | 58.51% | 58.51% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0 | tLTO (LTO jälkeinen lämpötila mitoitusolosuhteessa) |  | 17.451
KS. säädata | Maa | 1 |  | 1 | -25 | 0 | 21 | -6.5 | -6.5 | -6.5 | -17.226 | 21 | 2.5 | 13.226 | 1 | 59.78% | 59.78% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
välilehti | Vyöhyke | 1 |  | 1 | -24 | 0 | 21 | -6.5 | -6.5 | -6.5 | -16.395 | 21 | 3.5 | 13.395 | 1 | 61.11% | 61.11% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0 | Jälkilämmityspatterin ottoteho |  | 532.35 | W
| Muut poistoilmavirrat ei LTO:n kautta | 0 | l/s |  | -23 | 0 | 21 | -6.5 | -6.5 | -6.5 | -15.564 | 21 | 4.5 | 13.564 | 1 | 62.5% | 62.5% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0 |  | Tulostus | 532.35 | W
| Käyttöaika / vrk | 0 | h |  | -22 | 0 | 21 | -6.5 | -6.5 | -6.5 | -14.733 | 21 | 5.5 | 13.733 | 1 | 63.95% | 63.95% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
| Poistoilma, kaikki | 125 | l/s |  | -21 | 0 | 21 | -6.5 | -6.5 | -6.5 | -13.902 | 21 | 6.5 | 13.902 | 1 | 65.48% | 65.48% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
| Koko IV:n RT | 1 |  |  | -20 | 0 | 21 | -6.5 | -6.5 | -6.5 | -13.071 | 21 | 7.5 | 14.071 | 1 | 67.07% | 67.07% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
HUOM! | Mitoittava ulkoLT | -26 | °C |  | -19 | 0 | 21 | -6.5 | -6.5 | -6.5 | -12.24 | 21 | 8.5 | 14.24 | 1 | 68.75% | 68.75% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
| Tuloilman LT, mit. | 1.5 | °C |  | -18 | 0 | 21 | -6.5 | -6.5 | -6.5 | -11.409 | 21 | 9.5 | 14.409 | 1 | 70.51% | 70.51% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
[5 empty] | -17 | 0 | 21 | -6.5 | -6.5 | -6.5 | -10.578 | 21 | 10.5 | 14.578 | 1 | 72.37% | 72.37% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
[5 empty] | -16 | 0 | 21 | -6.5 | -6.5 | -6.5 | -9.747 | 21 | 11.5 | 14.747 | 1 | 74.32% | 74.32% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
[5 empty] | -15 | 0 | 21 | -6.5 | -6.5 | -6.5 | -8.916 | 21 | 12.5 | 14.916 | 1 | 76.39% | 76.39% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
| VUOSIHYÖTYSUHDE |  | 83.1% |  | -14 | 0 | 21 | -6.5 | -6.5 | -6.5 | -8.085 | 21 | 13.5 | 15.085 | 1 | 78.57% | 78.57% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
[5 empty] | -13 | 0 | 21 | -6.5 | -6.5 | -6.5 | -7.254 | 21 | 14.5 | 15.254 | 1 | 80.88% | 80.88% | 83.1% | 83.1% | 0 | 0 | 0 | 0 | 0
[5 empty] | -12 | 0.00034247 | 21 | -6.423 | -6.423 | -6.423 | -6.423 | 21 | 15.423 | 15.423 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 4.125 | 3.4279 | 3.4279 | 14.9391 | 12.4144
[5 empty] | -11 | 0.0013699 | 21 | -5.592 | -5.592 | -5.592 | -5.592 | 21 | 15.592 | 15.592 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 12 | 9.972 | 9.972 | 43.4592 | 36.1146
[5 empty] | -10 | 0.0049087 | 21 | -4.761 | -4.761 | -4.761 | -4.761 | 21 | 15.761 | 15.761 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 40.0417 | 33.2746 | 33.2746 | 145.0149 | 120.5074
[5 empty] | -9 | 0.0067352 | 21 | -3.93 | -3.93 | -3.93 | -3.93 | 21 | 15.93 | 15.93 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 20 | 16.62 | 16.62 | 72.432 | 60.191
[5 empty] | -8 | 0.0091324 | 21 | -3.099 | -3.099 | -3.099 | -3.099 | 21 | 16.099 | 16.099 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 25.375 | 21.0866 | 21.0866 | 91.8981 | 76.3673
| Tuloilman rajoitus (muutos v.6.0) |  |  |  | -7 | 0.011301 | 21 | -2.268 | -2.268 | -2.268 | -2.268 | 21 | 16.268 | 16.268 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 22.1667 | 18.4205 | 18.4205 | 80.2788 | 66.7117
| No limitation |  |  |  | -6 | 0.023858 | 21 | -1.437 | -1.437 | -1.437 | -1.437 | 21 | 16.437 | 16.437 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 123.75 | 102.8362 | 102.8362 | 448.173 | 372.4318
| Limited |  |  |  | -5 | 0.042922 | 21 | -0.606 | -0.606 | -0.606 | -0.606 | 21 | 16.606 | 16.606 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 180.9167 | 150.3417 | 150.3417 | 655.2078 | 544.4777
| Valinta | 1 |  |  | -4 | 0.056849 | 21 | 0.225 | 0.225 | 0.225 | 0.225 | 21 | 16.775 | 16.775 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 127.0833 | 105.6063 | 105.6063 | 460.245 | 382.4636
|  | No limitation |  |  | -3 | 0.080936 | 21 | 1.056 | 1.056 | 1.056 | 1.056 | 21 | 16.944 | 16.944 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 211 | 175.341 | 175.341 | 764.1576 | 635.015
[5 empty] | -2 | 0.11107 | 21 | 1.887 | 1.887 | 1.887 | 1.887 | 21 | 17.113 | 17.113 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 253 | 210.243 | 210.243 | 916.2648 | 761.416
| Tuloilma rajoitus | FALSE |  |  | -1 | 0.15719 | 21 | 2.718 | 2.718 | 2.718 | 2.718 | 21 | 17.282 | 17.282 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 370.3333 | 307.747 | 307.747 | 1341.1992 | 1114.5365
| Syöttöarvon muotoilu | TRUE |  |  | 0 | 0.21256 | 21 | 3.549 | 3.549 | 3.549 | 3.549 | 21 | 17.451 | 17.451 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 424.375 | 352.6556 | 352.6556 | 1536.9165 | 1277.1776
[5 empty] | 1 | 0.24155 | 21 | 4.38 | 4.38 | 4.38 | 4.38 | 21 | 17.62 | 17.62 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 211.6667 | 175.895 | 175.895 | 766.572 | 637.0213
| Sisälämpötila | 21 |  |  | 2 | 0.30034 | 21 | 5.211 | 5.211 | 5.211 | 5.211 | 21 | 17.789 | 17.789 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 407.7083 | 338.8056 | 338.8056 | 1476.5565 | 1227.0185
| Maksimi asetus | 20 |  |  | 3 | 0.34852 | 21 | 6.042 | 6.042 | 6.042 | 6.042 | 21 | 17.958 | 17.958 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 316.5 | 263.0115 | 263.0115 | 1146.2364 | 952.5224
| Max tLTO valinta | 21 |  |  | 4 | 0.40251 | 21 | 6.873 | 6.873 | 6.873 | 6.873 | 21 | 18.127 | 18.127 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 335.0417 | 278.4196 | 278.4196 | 1213.3869 | 1008.3245
[5 empty] | 5 | 0.44121 | 21 | 7.704 | 7.704 | 7.704 | 7.704 | 21 | 18.296 | 18.296 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 226 | 187.806 | 187.806 | 818.4816 | 680.1582
| Huomioteksti |  |  |  | 6 | 0.46187 | 21 | 8.535 | 8.535 | 8.535 | 8.535 | 21 | 18.465 | 18.465 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 113.125 | 94.0069 | 94.0069 | 409.6935 | 340.4553
| FALSE |  |  |  | 7 | 0.50445 | 21 | 9.366 | 9.366 | 9.366 | 9.366 | 21 | 18.634 | 18.634 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 217.5833 | 180.8118 | 180.8118 | 787.9998 | 654.8278
| Huom. YM monisteen 122 mukaisesti laskettuna tuloilman maksimilämpötilan rajoitus voi olla käytössä tai sitä ei tarvitse huomioida. Todellisuudessa rakennuksen energiankulutusta arvioitaessa tulee huomioida, että kaikkea kennon talteenottamaa lämpöenergiaa ei voida hyödyntää. |  |  |  | 8 | 0.54589 | 21 | 10.197 | 10.197 | 10.197 | 10.197 | 21 | 18.803 | 18.803 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 196.625 | 163.3954 | 163.3954 | 712.0971 | 591.7527
[5 empty] | 9 | 0.58037 | 21 | 11.028 | 11.028 | 11.028 | 11.028 | 21 | 18.972 | 18.972 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 151 | 125.481 | 125.481 | 546.8616 | 454.442
[5 empty] | 10 | 0.6218 | 21 | 11.859 | 11.859 | 11.859 | 11.859 | 21 | 19.141 | 19.141 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 166.375 | 138.2576 | 138.2576 | 602.5437 | 500.7138
[5 empty] | 11 | 0.64635 | 21 | 12.69 | 12.69 | 12.69 | 12.69 | 21 | 19.31 | 19.31 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 89.5833 | 74.4438 | 74.4438 | 324.435 | 269.6055
[5 empty] | 12 | 0.69669 | 21 | 13.521 | 13.521 | 13.521 | 13.521 | 21 | 19.479 | 19.479 | 1 | 83.1% | 83.1% | 83.1% | 83.1% | 165.375 | 137.4266 | 137.4266 | 598.9221 | 497.7043
[23 empty] | 15973.9722 | 13274.3709
[5 empty] | Jälkilämmityspatterin ottotehon mitoitukseen | [17 empty] | kWh | kWh
[5 empty] | 0 | [7 empty] | 17.451 | [10 empty] | 83.1%
[9 empty] | 33 | 0 | 17.451
[9 empty] | 34 | 1 | 17.62

## Kirjasto (hidden)
Versio | 7.3 | [5 empty] | Korjattu Airfi:lta 25.9.2024 saadun kommenttiexcelin perusteella (37/152 korjattua --> 25% pielessä)
| Kielivalinta: |  | 1. SUOMI | 2. ENGLANTI | 3. RUOTSI | 4. SAKSA | 5. PUOLA | 6. VIRO | 7. LATVIA | 8. LIETTUA | Taulukot: | Tulostusvälilehden ohjauksia, jos kielivalinta suomi
| 2 | 1 | Versio 7.3 | Version 7.3 | Version 7.3 | Version 7.3 | Wersja 7.3 | Versioon 7.3 | Versija 7.3 | 7.3 versija
|  | 2 | Airfi: ilmanvaihtokoneen valintaohjelma | Airfi: air handling unit selection program | Airfi: produktvalprogram för ventilationsaggregat | Airfi: Auswahlprogramm für Lüftungsgeräte | Airfi: program doborowy urządzeń wentylacyjnych | Airfi: ventilatsiooniseadme valimise tarkvara | Airfi: ventilācijas iekārtas izvēles programma | Airfi: vėdinimo įrangos parinkties programa | Pressure difference [Pa] | Suomi valittu | FALSE
|  | 3 | Kohde: | Project: | Projekt: | Projekt: | Obiekt: | Objekt: | Objekts: | Objektas: | Air volume flow [dm³/s] | Suomi ei valittu | TRUE
|  | 4 | Suunnittelija: | Name: | Namn: | Designer: | Projektant: | Projekteerija: | Projektētājs: | Projektuotojas: | Air volume flow [m³/h]
|  | 5 | Valitse malli: | Select model: | Välj modell: | Modell wählen: | Wybierz model: | Vali mudel: | Izvēlēties modeli: | Pasirinkti modelį: | Supply air temperature after heat exchanger
|  | 6 | Äänenvaimennuskotelo: 'dB-paketti' (Huom! Vaatii kaappirungon) | Sound insulated casing: "dB-paketti" (NB! Requires a cabinet) | Ljudisolerat hölje: "dB-paketti" (Obs! Kräver en skåpram) | Schallgedämmtes Gehäuse: "dB-paketti" (N.B. Braucht einen Schrankrahmen) | Obudowa tłumiąca dźwięk: "pakiet dB" (Uwaga! Wymaga ramy szafki) | Mürasummutuskate: 'dB-pakett' (NB! Nõuab kapiraami) | Skaņu slāpējošs korpuss: 'dB-pakete' (Uzmanību! Nepieciešams skapja korpuss) | Garso slopinimo gaubtas: „dB paketas“ (Dėmesio! Reikalingas rėminis korpusas) | Supply air temperature [°C]
|  | 7 | Vesikiertoinen lämmityspatteri | Post heating water | Värmebatteri | Wasser-Heizregister | Nagrzewnica wodna | Veeringlusega kalorifeer | Ūdens cirkulācijas apsildes radiators | Šildymo radiatorius su vandens cirkuliacija | Outdoor air temperature [°C]
|  | 8 | Ei käytettävissä tässä mallissa | Not available for the selected model | Ej tillgänglig för denna modell | Für das ausgewählte Modell nicht verfügbar | Niedostępne w tym modelu | Ei ole selle mudeli puhul kasutatav | Šim modelim nav izmantojams | Šiame modelyje nėra
|  | 9 | Pistotulppa 230 V, 50 Hz, 10 A, max 1165 W | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1165 W | Stecker 230 V, 50 Hz, 10 A, max 1165 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1165 W | Pistik 230 V, 50 Hz, 10 A, max 1165 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1165 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1165 W | Exhaust air temperature
|  | 10 | Pistotulppa 230 V, 50 Hz, 10 A, max 1165 W | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1165 W | Stecker 230 V, 50 Hz, 10 A, max 1165 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1165 W | Pistik 230 V, 50 Hz, 10 A, max 1165 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1165 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1165 W | Exhaust air temperature [°C]
|  | 11 | Pistotulppa 230 V, 50 Hz, 16 A, max 2200 W | Electric plug 230 V, 50 Hz, 16 A, max 2200 W | Stickkontakt 230 V, 50 Hz, 16 A, max 2200 W | Stecker 230 V, 50 Hz, 16 A, max 2200 W | Wtyczka 230 V, 50 Hz, 16 A, maks. 2200 W | Pistik 230 V, 50 Hz, 16 A, max 2200 W | Kontaktspraudnis 230 V, 50 Hz, 16 A, maks. 2200 W | Kištukas 230 V, 50 Hz, 16 A, maks. 2200 W | Outdoor air temperature [°C]
|  | 12 | Pistotulppa 230 V, 50 Hz, 16 A, max 3500 W | Electric plug 230 V, 50 Hz, 16 A, max 3500 W | Stickkontakt 230 V, 50 Hz, 16 A, max 3500 W | Stecker 230 V, 50 Hz, 16 A, max 3500 W | Wtyczka 230 V, 50 Hz, 16 A, maks. 3500 W | Pistik 230 V, 50 Hz, 16 A, max 3500 W | Kontaktspraudnis 230 V, 50 Hz, 16 A, maks. 3500 W | Kištukas 230 V, 50 Hz, 16 A, maks. 3500 W
|  | 13 | Pistotulppa 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Electric plug 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Stickkontakt 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Stecker 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Wtyczka 400 VAC, 50 Hz, 3 x 16 A, maks. 8250 W | Pistik 400 V AC, 50 Hz, 3 x 16 A, max 8250 W | Kontaktspraudnis 400 VAC, 50 Hz, 3 x 16 A, maks. 8250 W | Kištukas 400 VAC, 50 Hz, 3 x 16 A, maks. 8250 W | Air density: 1.2 kg/m³
|  | 14 | Pistotulppa 230 V, 50 Hz, 10 A, max 1255 W | Electric plug 230 V, 50 Hz, 10 A, max 1255 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1255 W | Stecker 230 V, 50 Hz, 10 A, max 1255 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1255 W | Pistik 230 V, 50 Hz, 10 A, max 1255 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1255 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1255 W | Supply air
|  | 15 | Ilman tiheys: 1,2 kg/m³ | Air density: 1.2 kg/m³ | Lufttäthet: 1,2 kg/m³ | Luftdichte: 1,2 kg/m³ | Gęstość powietrza: 1,2 kg/m³ | Õhu tihedus: 1,2 kg/m³ | Gaisa blīvums: 1,2 kg/m³ | Oro tankis: 1,2 kg/m³ | Extract air
|  | 16 | Tuloilma | Supply air | Tilluft | Zuluft | Powietrze nawiewane | Sissepuhkeõhk | Ieplūstošais gaiss | Tiekiamas oras
|  | 17 | Poistoilma | Extract air | Frånluft | Abluft | Powietrze wywiewane | Väljatõmbeõhk | Izplūstošais gaiss | Ištraukiamas oras | Sound insulated casing: "dB-paketti" (NB! Requires a cabinet)
|  | 18 | Paine-ero [Pa] | Pressure difference [Pa] | Tryckskillnad [Pa] | Druckdifferenz [Pa] | Różnica ciśnień [Pa] | Rõhuerinevus [Pa] | Spiedienu starpība [Pa] | Slėgio skirtumas [Pa] | Post heating water
|  | 19 | Ilman tilavuusvirta [dm³/s] | Air volume flow [dm³/s] | Luftens volymflöde [dm³/s] | Luftvolumenstrom [dm³/s] | Natężenie przepływu powietrza [dm³/s] | Õhu vooluhulk [dm³/s] | Gaisa tilpuma plūsma [dm³/s] | Oro srautas [dm³/s]
|  | 20 | Tuloilma (syötä arvot): | Supply air (insert values): | Tilluft (fyll i värden): | Zuluft (Werte eingeben): | Nawiewane powietrze (wprowadzić wartości): | Sissepuhkeõhk (sisesta väärtused): | Ieplūstošais gaiss (ievadīt vērtības): | Tiekiamas oras (įveskite vertes):
|  | 21 | Ilman tilavuusvirta: | Air volume flow: | Luftens volymflöde: | Luftvolumenstrom: | Natężenie przepływu powietrza | Õhu vooluhulk: | Gaisa tilpuma plūsma: | Oro srautas:
|  | 22 | Paine-ero: | Pressure difference: | Tryckskillnad: | Druckdifferenz [Pa] | Różnica ciśnień: | Rõhuerinevus | Spiedienu starpība: | Slėgio skirtumas:
|  | 23 | Ei käyttöalueella | Value out of range | Värde utanför området | Werte überprüfen | Nie w obszarze użytkowania | Pole kasutusalas | Nav ekspluatācijas diapazonā | Naudojimo zonoje nėra
|  | 24 | Poistoilma (syötä arvot): | Extract air (insert values): | Frånluft (fyll i värden): | Abluft (Werte eingeben): | Powietrze wylotowe (wprowadzić wartości): | Väljatõmbeõhk (sisestage väärtused): | Izplūstošais gaiss (ievadīt vērtības): | Ištraukiamas oras (įveskite vertes):
|  | 25 | Tulopuhallin: | Supply fan: | Tilluftsfläkt: | Zuluftsventilator: | Wentylator nawiewny: | Sissepuhkeventilaator: | Ieplūstošā gaisa ventilators: | Įsiurbimo ventiliatorius:
|  | 26 | Ohjausjännite: | Control voltage: | Styrspänning: | Steuerspannung: | Napięcie sterowania: | Juhtpinge: | Vadības spriegums: | Valdymo įtampa:
|  | 27 | Puhaltimen ottoteho: | Fan power: | Fläktens ineffekt: | Eingangsleistung: | Moc wentylatora: | Ventilaatori võimsustarve: | Ventilatoru ieejas jauda: | Ventiliatorių įsiurbimo galia:
|  | 28 | Poistopuhallin: | Extract fan: | Frånluftsfläkt: | Abluftsventilator: | Wentylator wyciągowy: | Väljatõmbeventilaator: | Izplūstošā gaisa ventilators: | Ištraukiamasis ventiliatorius:
|  | 29 | Kokonaisteho: | Total power: | Totaleffekt: | Gesamtleistung: | Całkowita moc: | Koguvõimsus: | Kopējā jauda: | Bendra galia:
|  | 30 | SFP: | SFP: | SFP: | SFP: | SFP: | SFP: | SFP: | SFP:
|  | 31 | Äänitehotasot liitäntäkanavissa | Sound power levels in connection ducts | Ljudeffektnivåer i kanalmynningarna | Schallleistungspegel in Anschlusskanäle | Poziomy mocy akustycznej w kanałach przyłączeniowych | Helivõimsustasemed ühenduskanalites | Skaņas jaudas līmeņi savienotājkanālos | Garso galios lygis jungiamajame kanale
|  | 32 | Liitäntäkanava | Connection duct | Kanalmynning | Anschlusskanal | Kanał przyłączeniowy | Ühenduskanal | Pieslēguma kanāli | Jungiamasis kanalas
|  | 33 | Tuloilma | Supply air | Tilluft | Zuluft | Nawiew | Sissepuhkeõhk | Ieplūstošais gaiss | Tiekiamas oras
|  | 34 | Ulkoilma | Outdoor air | Uteluft | Außenluft | Czerpnia | Välisõhk | Āra gaiss | Lauko oras
|  | 35 | Poistoilma | Extract air | Frånluft | Abluft | Wywiew | Väljatõmbeõhk | Izplūstošais gaiss | Ištraukiamas oras
|  | 36 | Jäteilma | Exhaust air | Avluft | Fortluft | Wyrzutnia | Heitõhk | Piesārņotais gaiss | Išeinantis oras
|  | 37 | Keittiöohitus | Kitchen bypass | Förbigång för kök | Küchen Bypass | Bypass okapu kuchennego | Köögi möödaviik | Virtuves apeja | Virtuvės aplenkimas
|  | 38 | Äänitehotasot oktaavikaistoittain LW,okt [dB] | Sound power levels in octave bands LW,oct [dB] | Ljudeffektnivåer i oktavband LW,okt [dB] | Schallleistungspegel in Oktavbändern LW,okt [dB] | Poziomy mocy akustycznej w paśmie oktawowym LW,oct [dB] | Helivõimsuse tasemed oktaaviribade kaupa LW,okt [dB] | Skaņas jaudas līmeņi pa oktāvas joslām LW,okt [dB] | Garso galios lygiai pagal oktavų juostas LW,okt [dB]
|  | 39 | LWtot | LWtot | LWtot | LWtot | LWtot | LWtot | LWtot | LWtot
|  | 40 | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot
|  | 41 | Äänitehotasot ympäristöön | Sound power levels through casing: | Ljudeffektnivå till omgivningen | Schallleistungspegel durch das Gehäuse | Poziom mocy akustycznej generowany do otoczenia | Helivõimsuse tasemed keskkonnas | Skaņas jaudas līmeņi vidē | Garso galios lygiai aplinkoje
|  | 42 | Vaipan läpi | Through casing | Genom manteln | Durch das Gehäuse | Przez obudowę | Läbi katte | Caur apvalku | Per vožtuvą
|  | 43 | Äänipainetaso huonetilassa, jonka ääniabsorptioala 10m²: | Sound pressure level in a room with an absorption area of 10m²: | Ljudtrycksnivå i ett rum, vars ljudabsorptionsarea är 10m²: | Schalldruckpegel im Raum mit einer Absorptionsfläche von 10m² | Poziom ciśnienia akustycznego w pomieszczeniu o powierzchni pochłaniania dźwięku wynoszącej 10 m²: | Helirõhutase ruumis, mille heli neeldumispind on 10 m²: | Skaņas spiediena līmenis telpā, kuras skaņas absorbcijas platība ir 10 m²: | Garso slėgio lygis patalpoje, kurios garso sugerties plotas yra 10 m²:
|  | 44 | Äänipainetaso tyypillisessä kylpyhuoneessa tai tekn. tilassa (V < 10 m³), jonka ääniabsorptioala < 2-3 m²: | Sound pressure level in a typical bathroom (V < 10 m³) with an absorption area < 2-3 m²: | Ljudtrycksnivå i ett typiskt badrum (V < 10 m³), vars ljudabsorptionsarea är < 2-3 m² | Schalldruckpegel in typischem Badezimmer (V < 10 m³) mit einer Absorptionsfläche < 2-3 m²: | Poziom ciśnienia akustycznego w typowej łazience lub pomieszczeniu technicznym (V < 10 m³) o powierzchni pochłaniania dźwięku < 2-3 m²: | Helirõhutase tüüpilises vannitoas või tehnoruumis (V < 10 m³), mille heli neeldumispind on < 2-3 m²: | Skaņas spiediena līmenis tipiskā vannas istabā vai tehniskajā telpā (V < 10 m³), kuras skaņas absorbcijas platība ir < 2-3 m²: | Garso slėgio lygis įprastame vonios kambaryje arba techninėje patalpoje (V < 10 m³), kurios garso sugerties plotas < 2-3 m²:
|  | 45 | Ominaisenergiankulutus (SEC) ja luokittelu | Specific energy consumption (SEC) and classification | Specifik energianvändning (SEC) och klassifikation | Spezifischer Energieverbrauch (SEV) und Klassifizierung | Jednostkowe zużycie energii (SEC) i klasyfikacja | Spetsiifiline energiatarve (SEC) ja liigitus | Īpatnējais enerģijas patēriņš (Specific Energy Consumption — SEC) un klasifikācija | Savitasis energijos suvartojimas (SEC) ir klasifikacija
|  | 46 | Komission asetusten (EU) N:o 1253/2014 & N:o 1254/2014 mukaisesti | According to Commission Regulations (EU) No 1253/2014 & No 1254/2014 | I enlighet med kommisionens förordningar (EU) nr 1253/2014 & nr 1254/2014 | Entsprechend den Verdordnungen (EU) Nr. 1253/2014 & Nr. 1254/2014 der Kommission | Zgodnie z rozporządzeniami Komisji (UE) nr 1253/2014 i nr 1254/2014 | Vastavalt Euroopa Komisjoni määrustele (EL) nr 1253/2014 ja 1254/2014 | Saskaņā ar Komisijas Regulām (ES) Nr. 1253/2014 un Nr. 1254/2014 | Pagal Komisijos reglamentus (ES) Nr. 1253/2014 ir Nr. 1254/2014
|  | 47 | HUOM! SEC-laskentaa käytetään vain asuinrakennuksiin tarkoitetuilla ilmanvaihtokoneilla. | NB! SEC-calculation is only used for air handling units intended for residential buildings | Obs! SEC-beräkning används endast för ventilationsaggregat avsedda för bostadshus | NB! Die SEV-Berechnung wird nur für Wohnraumlüftungsanlage verwendet | UWAGA! Obliczenia SEC są stosowane tylko w przypadku urządzeń wentylacyjnych przeznaczonych do budynków mieszkalnych. | TÄHELEPANU! SEC arvutust kasutatakse ainult eluhoonetes kasutatavate ventilatsiooniseadmete puhul. | UZMANĪBU! SEC aprēķinu izmanto tikai dzīvojamajām ēkā paredzētajām ventilācijas iekārtām. | DĖMESIO! SEC formulė taikoma tik gyvenamiesiems pastatams skirtiems vėdinimo įrenginiams.
|  | 48 | Vertailuilmavirta: | Reference air flow: | Referensluftflöde: | Nennluftvolumenstrom: | Referencyjny przepływ powietrza: | Võrdlusõhuvool: | References gaisa plūsma: | Lyginamasis oro srautas:
|  | 49 | Laskennan lähtöarvot: | Calculation parameters: | Beräkningsparametrar: | Berechnungsparameter: | Wartości wyjściowe dla obliczeń: | Arvutuse lähteväärtused: | Aprēķinu izejas vērtības: | Skaičiavimo pradinės vertės:
|  | 50 | Yleinen luokittelu | General typology | Allmän klassifiering | Allgemeine Typologie | Klasyfikacja ogólna | Üldine liigitus | Vispārīgā klasifikācija | Bendroji klasifikacija
|  | 51 | Ilmanvaihdon ohjaus | Ventilation control | Ventilationsstyrning | Lüftungssteuerung | Sterowanie wymianą powietrza | Ventilatsiooni juhtimine | Ventilācijas vadība | Vėdinimo valdymas
|  | 52 | Moottori ja ohjaus | Motor & drive | Motor & styrning | Motor und Antrieb | Silnik i układ sterowania | Mootor ja juhtimine | Motors un vadība | Variklis ir valdymas
|  | 53 | Ilmasto | Climate | Klimat | Klima | Klimat | Kliima | Klimats | Klimatas
|  | 54 | Kaikki oikeudet pidätetään. | All rights reserved. | Alla rättigheter förbehållna. | Alle Rechte vorbehalten. | Wszelkie prawa zastrzeżone. | Kõik õigused on kaitstud. | Visas tiesības rezervētas. | Visos teisės saugomos.
|  | 55 | Sovelletut asiakirjat ja standardit: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Tasauslaskentaopas 2018, YM moniste 122 ja Komission asetukset (EU) N:o 1253/2014 & N:o 1254/2014. Emme vastaa ohjelman mahdollisista virheistä tai niiden aiheuttamista välittömistä tai välillisistä virheistä. | Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, "Tasauslaskentaopas 2018" & "Moniste 122", and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program. | Tillämpade dokument och standarder: SFS-EN 13141-7, LVI 30-10529, Finska Miljöministeriets förordning 1009/2017, "Tasauslaskentaopas 2018", Finska Miljöministeriets kompendium 122 samt kommisionens förordningar (EU) nr 1253//2014 & nr 1254/2014. Vi ansvarar inte för direkt eller indirekt skada orsakad av möjliga fel i produktvalprogrammet. | Angewandte Dokumente und Normen: SFS-EN 13141-7, LVI 30-10529, Finnisches Umweltministerium: Dekret 1009/2017, "Tasauslaskentaopas 2018" & "Moniste 122" und Verordnung (EU) Nr. 1253/2014 & 1254/2014 Der Kommission. Wir sind nicht verantwortlich für direkte oder indirekte Schäden, die durch mögliche Fehler im Auswahlprogramm verursacht werden. | Obowiązujące dokumenty i normy: SFS-EN 13141-7, LVI 30-10529, Rozporządzenie Ministerstwa Środowiska YMa1009/2017, Przewodnik bilansowania 2018, Publikacja Ministerstwa Środowiska YM 122 oraz rozporządzenia Komisji (UE) nr 1253/2014 i nr 1254/2014. Nie ponosimy odpowiedzialności za jakiekolwiek błędy w programie ani za jakiekolwiek bezpośrednie lub pośrednie błędy przez nie spowodowane. | Kohaldatud dokumendid ja standardid: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Ühtlustamisarvutuste juhend 2018, YM paljundus 122 ja Komisjoni määrused (EL) nr 1253/2014 ja nr 1254/2014. Me ei vastuta tarkvara võimalike puuduste ega nendest tulenevate otseste või kaudsete vigade eest. | Izmantotie dokumenti un standarti: SFS-EN 13141-7, LVI 30-10529, Vides ministrijas dekrēts 1009/2017, Balansēšanas aprēķina rokasgrāmata 2018, Vides ministrijas kopija Nr. 122 un Komisijas Regulas (ES) Nr. 1253/2014 un Nr. 1254/2014. Nenesam atbildību par iespējamām kļūdām programmā vai to izraisītām tiešām vai netiešām kļūdām. | Taikyti dokumentai ir standartai: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, 2018 m. skaičiavimo vadovas, Aplinkos ministerijos leidinys 122 ir Komisijos reglamentai (ES) Nr. 1253/2014 ir Nr. 1254/2014. Neatsakome už jokias programos klaidas ar dėl jų atsiradusias tiesiogines ar netiesiogines paklaidas.
|  | 56 | Laskentaohjelman laatinut Insinööritoimisto W. Zenner Oy. Laskentaohjelma perustuu SFS-EN 13141-7 mukaisiin laboratoriomittauksiin. | The selection program is made by Insinööritoimisto W. Zenner Oy. The program is based on laboratory measurements according to SFS-EN 13141-7. | Produktvalprogrammet har gjorts av Insinööritoimisto W. Zenner Oy. Programmet baserar sig på laboratoriemätningar i enlighet med SFS-EN 13141-7. | Auswahlprogramm ist von Insinööritoimisto W. Zenner Oy erstellt. Das Programm basiert auf Labormessungen nach SFS-EN 13141-7. | Program obliczeniowy został przygotowany przez W. Zenner Oy. Program obliczeniowy oparty jest na pomiarach laboratoryjnych zgodnie z normą SFS-EN 13141-7. | Arvutusprogrammi on koostanud Insinööritoimisto W. Zenner Oy. Arvutusprogramm põhineb standardile SFS-EN 13141-7 vastavatel laboratoorsetel mõõtmistel. | Aprēķinu programmu sagatavoja inženieru birojs Insinööritoimisto W. Zenner Oy. Aprēķinu programmas pamatā ir saskaņā ar SFS-EN 13141-7 veikti laboratorijas mērījumi. | Skaičiavimo programą parengė inžinierių biuras „W. Zenner Oy“. Skaičiavimo programa grindžiama laboratoriniais matavimais pagal SFS-EN 13141-7.
|  | 57 | SEC-luku | SEC-value | SEC-värde | SEV-Wert | Numer SEC | SEC arv | SEC skaitlis | SEC numeris
|  | 58 | Luokka | Class | Klass | Klasse | Klasa | Klass | Klase | Kategorija
|  | 59 | Kanavaliitäntäinen | Ducted units | Kanalansluten enhet | Anlagen mit Kanalanschlußstutzen | Powiązany z kanałem | Kanaliühendusega | Pieslēdzams kanālam | Su jungiamuoju kanalu
|  | 60 | Muu kuin kanavaliitäntäinen | Non-ducted units | Icke kanalansluten enhet | Anlagen ohne Kanalanschlußstutzen | Inne niż powiązane z kanałem | Muu kui kanaliühendusega | Kanālam nepieslēdzams | Su kitokiu, o ne jungiamuoju kanalu
|  | 61 | Käsikäyttö (ei tarp.muk. IV) | Manual control (no DCV) | Manuell styrning (ej behovsstyrd ventilation) | Handsteuerung (keine Bedarfssteuerung) | Obsługa ręczna (niewymagana) IV) | Käsikasutus (mittevajaduspõhine ventilatsioon) | Manuāla vadība (ne pēc vajadzības IV) | Rankinis valdymas (ne pagal poreikį IV)
|  | 62 | Kello-ohjaus (ei tarp.muk. IV) | Clock control (no DCV) | Klockstyrning (ej behovsstyrd ventilation) | Zeitsteuerung (keine Bedarfssteuerung) | Sterowanie zegarem (niewymagane) IV) | Kelljuhtimine (mittevajaduspõhine ventilatsioon) | Pulksteņvadība (ne pēc vajadzības IV) | Laikrodinis valdymas (ne pagal poreikį IV)
|  | 63 | Keskitetty tarp.muk. ohjaus | Central demand control | Central behovsstyrning | Zentrale Bedarfssteuerung | Scentralizowana kontrola w zależności od potrzeb | Tsentraalne vajaduspõhine juhtimine | Centralizēta vadība pēc vajadzības | Centralizuotas valdymas pagal poreikį
|  | 64 | Paikallinen tarp.muk. ohjaus | Local demand control | Lokal behovsstyrning | Steuerung nach örtlichem Bedarf | Lokalna kontrola w zależności od potrzeb | Kohalik vajaduspõhine juhtimine | Vietēja vadība pēc vajadzības | Vietinis valdymas pagal poreikį
|  | 65 | On/off & yksinopeuksinen | On/off & single speed | On/Off & enkelhastighets | Ein/aus und eine Drehzahl | Włączanie/wyłączanie i pojedyncza prędkość | Sisse/välja ja ühekiiruseline | Ieslēgts/izslēgts un vienātruma | Įjungta/išjungta ir vienas greitis
|  | 66 | Kaksinopeuksinen | 2-speed | 2-hastighets | 2 Drehzahlen | Dwubiegowy | Kahekiiruseline | Divātrumu | Du greičiai
|  | 67 | Moninopeuksinen | Multi-speed | Flerhastighets | mehrere Drehzahlen | Wieloprędkościowy | Mitmekiiruseline | Vairākātrumu | Daugiau greičių
|  | 68 | Portaaton säätö | Variable-speed | Steglös reglering | regelbare Drehzahl | Bezstopniowa regulacja | Sujuv reguleerimine | Bezpakāpju regulēšana | Tolygus reguliavimas
|  | 69 | Kylmä | Cold | Kall | Kalt | Zimny | Külm | Auksts | Šalta
|  | 70 | Keskiarvo | Average | Medelvärde | Durchschnitt | Umiarkowany | Keskmine | Vidējs | Vidutinė vertė
|  | 71 | Lämmin | Warm | Varm | Warm | Ciepły | Soe | Silts | Šilta
|  | 72 | Ilmanvaihdon poistoilman lämmöntalteenoton vuosihyötysuhteen laskenta | Calculation of annual efficiency for exhaust air heat recovery | Beräkning av årsverkningsgrad för värmeåtervinning av ventilationens frånluft | Berechnung des Jahresnutzungsgrades der Wärmerückgewinnung der Lüftungsabluft | Obliczanie rocznej sprawności odzysku ciepła z powietrza wywiewanego z wentylacji | Ventilatsiooni väljatõmbeõhu soojusvahetuse aastase kasuteguri arvutamine | Ventilācijas izplūstošā gaisa rekuperācijas ikgadējā lietderības koeficienta aprēķināšana | Metinio šilumos atgavimo iš ištraukiamo oro efektyvumo apskaičiavimas
|  | 73 | Laskenta YM:n Monisteen 122 mukaisesti | Calculations according to Handout 122 of the Finnish Ministry of the Environment | Beräkning enligt Finska Miljöministeriets kompendium 122 | Berechnungen gemäß Handout 122 des finnischen Umweltministeriums | Obliczenia zgodnie z Publikacją Ministerstwa Środowiska YM 122 | Arvutamine YM-i trükise 122 kohaselt | Aprēķins saskaņā ar Vides ministrijas kopiju Nr. 122 | Skaičiavimas pagal Aplinkos ministerijos leidinį Nr. 122
|  | 74 | = syötettävä solu | = insert value | = Infoga värde | = Wert eingeben | = wprowadzana komórka | = sisestatav lahter | = ievadāmais lauciņš | = įvesties langelis
|  | 75 | Laskennan lähtöarvot: | Calculation parameters: | Beräkningsparametrar: | Berechnungsparameter: | Wartości wyjściowe dla obliczeń: | Arvutuse lähteväärtused: | Aprēķinu izejas vērtības: | Skaičiavimo pradinės vertės:
|  | 76 | Tuloilmavirta, LTO:n läpi virtaava | Supply air volume flow, through heat recovery | Tilluftsflöde, genom värmeåtervinningssystem | Zuluft, die durch die Wärmerückgewinnung strömt | Przepływ powietrza nawiewanego przez wymiennik odzysku ciepła | Sissepuhkeõhu vooluhulk, läbi soojusvaheti | Ieplūstošā gaisa plūsma, caur rekuperatoru plūstošā | Tiekiamo oro srautas, tekantis per LTO
|  | 77 | Poistoilmavirta, LTO:n läpi virtaava | Extract air volume flow, through heat recovery | Frånluftsflöde, genom värmeåtervinningssystem | Abluft, die durch die Wärmerückgewinnung strömt | Przepływ powietrza wywiewanego przez wymiennik odzysku ciepła | Väljatõmbeõhu vooluhulk, läbi soojusvaheti | Izplūstošā gaisa plūsma, caur rekuperatoru plūstošā | Ištraukiamo oro srautas, tekantis per LTO
|  | 78 | LTO:n läpi virtaavan tulo- ja poistoilmavirran suhde | Supply air to extract air ratio for volume flow through heat recovery | Förhållande av till- och frånluftsflöde genom värmeåtervinningen. | Das Verhältnis von Zuluft und Abluft Ströme durch die Wärmerückgewinnung | Stosunek przepływu powietrza nawiewanego i wywiewanego przez wymiennik odzysku ciepła | Läbi soojusvaheti voolava sissepuhkeõhu ja väljapuhkeõhu vooluhulga suhe | Caur rekuperatoru plūstošās ieplūstošās un izplūstošās gaisa plūsmas attiecība | Tiekiamo ir ištraukiamo oro srauto per LTO santykis
|  | 79 | LTO-vaatimuksen piiriin kuuluva erillispoistoilmavirta | Additional extract air flow rate included in heat recovery requirements | Ytterligare frånluft ingår i värmeåtervinningskraven | Zusatsabluft in den Wärmerückgewinnungsanforderungen enthalten | Dodatkowy przepływ powietrza wywiewanego trafiający na wymiennik odzysku ciepła | Soojusvaheti nõude alla kuuluv väljatõmbeõhu eriõhuvool | Rekuperatora darbības prasībās ietvertā atsevišķā izplūstošā gaisa plūsma | Atskiras ištraukiamo oro srautas, kuriam taikomas LTO reikalavimas
|  | 80 | Em. erillispoistoilman käyttöaika | Operational time of the additional extract air | Drifttid för ovan nämnda extra frånluft | Betriebsdauer der obenkenannten zusätzlichen Abluft | Czas korzystania z powyższego oddzielnego wyciągu powietrza | Näiteks eriväljatõmbeõhu kasutusaeg | Iepriekš minētās atsevišķās izplūstošās gaisa plūsmas izmantošanas laiks | Minėto atskiro ištraukiamo oro naudojimo laikas
|  | 81 | Koko IV:n tulo- ja poistoilmavirtojen suhde | Supply / extract air volume flow ratio for entire ventilation system | Förhållande av till- och frånluftsflöde genom värmeåtervinningen. | Das Verhältnis von Zuluft und Abluft für das gesamte Lüftungssystem | Stosunek przepływów powietrza nawiewanego i wywiewanego dla całego systemu wentylacyjnego | Kogu ventilatsiooni sissepuhke ja väljatõmbe õhuvoolude suhe | Visu IV ieplūstošo un izplūstošo gaisa plūsmu attiecība | Tiekiamo ir ištraukiamo oro srautų santykis visame IV
|  | 82 | Tuloilman lämpötilahyötysuhde yhtä suurilla ilmavirroilla (EN 13141-7) | Supply side temperature ratio for balanced air flow (EN 13141-7) | Temperaturverkningsgrad för tilluft vid motsvarande luftflöde (EN 13141-7) | Zulufts Temperatureffizienz bei gleichen Luftströmen (EN 13141-7) | Wydajność temperaturowa powietrza nawiewanego przy równych przepływach powietrza (EN 13141-7) | Sissepuhkeõhu temperatuuri kasutegur samade õhuvoolude korral (EN 13141-7) | Ieplūstošā gaisa temperatūras pārneses lietderības koeficients vienlīdz lielām gaisa plūsmām (EN 13141-7) | Tiekiamo oro temperatūros efektyvumo koeficientas esant vienodiems oro srautams (EN 13141-7)
|  | 83 | Tuloilman lämpötilahyötysuhde | Supply side temperature ratio | Temperaturverkningsgrad för tilluft | Zulufts Temperatureffizienz | Wydajność temperaturowa powietrza nawiewanego | Sissepuhkeõhu temperatuuri kasutegur | Ieplūstošā gaisa temperatūras pārneses lietderības koeficients | Tiekiamo oro temperatūros efektyvumo koeficientas
|  | 84 | Säävyöhyke | Climate zone | Klimatzon | Klimazone | Strefa klimatyczna | Kliimavöönd | Meteoroloģiskā zona | Klimato juosta
|  | 85 | Sisälämpötila | Indoor temperature | Inomhustemperatur | Innenlufttemperatur | Temperatura wewnętrzna | Sisetemperatuur | Iekštelpu temperatūra | Vidaus temperatūra
|  | 86 | Minimi jäteilman lämpötila | Minimum exhaust air temperature | Minimitemperatur för avluft | Minimale Fortlufttemperatur | Minimalna temperatura powietrza wyrzucanego | Minimaalne heitõhu temperatuur | Piesārņotā gaisa minimālā temperatūra | Minimali išeinančio oro temperatūra
|  | 87 | Maksimi tuloilman lämpötila rajoitetussa tilanteessa | Maximum supply air temperature in a limited situation | Maximitemperatur för tilluft i ett begränsad läge | Maximale Zulufttemperatur in einer begrenzten Situation | Maksymalna temperatura powietrza nawiewanego w ograniczonej sytuacji | Maksimaalne sissepuhkeõhu temperatuur piiratud olukorras | Maksimālā ieplūstošā gaisa temperatūra ierobežotā situācijā | Didžiausia tiekiamo oro temperatūra ribotoje padėtyje
|  | 88 | Vuosihyötysuhde | Annual efficiency | Årsverkningsgrad | Jährliche Effizienz | Roczny współczynnik efektywności energetycznej | Aastane kasutegur | Gada lietderības koeficients | Metinis efektyvumo koeficientas
|  | 89 | Ilmanvaihdon kokonaisenergiantarve | Total energy demand for ventilation | Totalt energibehov för ventilation | Gesamtenergiebedarf für Lüftung | Całkowite zapotrzebowanie na energię dla wentylacji | Ventilatsiooni koguenergiavajadus | Kopējais ventilācijai nepieciešamās enerģijas daudzums | Bendras vėdinimo sistemos energijos poreikis
|  | 90 | Talteenotettu lämmitysenergia | Recovered heating energy | Återvunnen värmeenergi | Zurückgewonnene Heizenergie | Odzyskana energia grzewcza | Salvestatud kütteenergia | Rekuperētā siltumenerģija | Atgauta šilumos energija
|  | 91 | Tuloilman lämpötila LTO:n jälkeen | Supply air temperature after heat exchanger | Tilluftstemperatur efter värmeåtervinning | Zulufttemperatur nach Wärmerückgewinnung | Temperatura powietrza nawiewanego po LTO | Sissepuhkeõhu temperatuur pärast soojusvahetit | Ieplūstošā gaisa temperatūra pēc rekuperatora | Tiekiamo oro temperatūra po LTO
|  | 92 | Tuloilman lämpötila [°C] | Supply air temperature [°C] | Tilluftstemperatur [°C] | Zulufttemperatur [°C] | Temperatura powietrza nawiewanego [°C] | Sissepuhkeõhu temperatuur [°C] | Ieplūstošā gaisa temperatūra [°C] | Tiekiamo oro temperatūra [°C]
|  | 93 | Ulkoilman lämpötila [°C] | Outdoor air temperature [°C] | Uteluftstemperatur [°C] | Außenlufttemperatur [°C] | Temperatura powietrza zewnętrznego [°C] | Välisõhu temperatuur [°C] | Āra gaisa temperatūra [°C] | Lauko oro temperatūra [°C]
|  | 94 | Jäteilman lämpötila | Exhaust air temperature | Avluftstemperatur | Fortlufttemperatur | Temperatura zużytego powietrza | Heitõhu temperatuur | Piesārņotā gaisa temperatūra | Išeinančio oro temperatūra
|  | 95 | Jäteilman lämpötila [°C] | Exhaust air temperature [°C] | Avluftstemperatur [°C] | Fortlufttemperatur [°C] | Temperatura zużytego powietrza [°C] | Heitõhu temperatuur [°C] | Piesārņotā gaisa temperatūra [°C] | Išeinančio oro temperatūra [°C]
|  | 96 | Ulkoilman lämpötila [°C] | Outdoor air temperature [°C] | Uteluftstemperatur [°C] | Außenlufttemperatur [°C] | Temperatura powietrza zewnętrznego [°C] | Välisõhu temperatuur [°C] | Āra gaisa temperatūra [°C] | Lauko oro temperatūra [°C]
|  | 97 | Aika vuodessa | Percentage of the year | Tid av året i procent | Anteil des Jahres | Czas w roku | Aeg aastas | Laiks gadā | Metų laikas
|  | 98 | Jäteilman lämpötila | Exhaust air temperature | Avlufts-temperatur | Fortluft-temperatur | Temperatura zużytego powietrza | Heitõhu temperatuur | Piesārņotā gaisa temperatūra | Išeinančio oro temperatūra
|  | 99 | Tuloilman lämpötila | Supply air temperature | Tillufts-temperatur | Zuluft-temperatur | Temperatura powietrza nawiewanego | Sissepuhkeõhu temperatuur | Ieplūstošā gaisa temperatūra | Tiekiamo oro temperatūra
|  | 100 | Yhteensä | Total | Summa | Gesamt | Razem | Kokku | Kopā | Iš viso
|  | 101 | SS,Kd = sisä- ja ulkoilman lämpötilan välinen lämmöntarveluku, Kd | SI,Kd = heating degree days, between indoor air and outdoor air, Kd | SI,Kd = graddagstal, mellan inne- och uteluft, Kd | SI,Kd = Wärmesumme, Innenluft - Außenluft, Kd | SS,Kd = współczynnik rozszerzalności cieplnej między temperaturą powietrza wewnętrznego i zewnętrznego, Kd | SS,Kd = sise- ja välisõhu temperatuuri vaheline soojusvajadusarv, Kd | SS,Kd = iekštelpu un āra gaisa temperatūras savstarpējais nepieciešamā siltuma koeficients, Kd | SS, Kd = šilumos poreikio tarp patalpos ir lauko oro temperatūros koeficientas, Kd
|  | 102 | ST,Kd = tulo- ja ulkoilman lämpötilan välinen lämmöntarveluku, Kd | SS,Kd = heating degree days, between supply air and outdoor air, Kd | SS,Kd = graddagstal, mellan till- och uteluft, Kd | SZ,Kd = Wärmesumme, Zuluft - Außenluft, Kd | ST,Kd = współczynnik rozszerzalności cieplnej między temperaturą powietrza nawiewanego i zewnętrznego, Kd | SS,Kd = sissepuhkeõhu ja välisõhu temperatuuri vaheline soojusvajadusarv, Kd | ST,Kd = ieplūstošā un āra gaisa temperatūras savstarpējais nepieciešamā siltuma koeficients, Kd | ST, Kd = šilumos poreikio tarp tiekiamo ir lauko oro temperatūros koeficientas, Kd
|  | 103 | SJ,Kd = jäte- ja ulkoilman lämpötilan välinen lämmöntarveluku, Kd | SE,Kd = heating degree days, between exhaust air and outdoor air, Kd | SE,Kd = graddagstal, mellan från- och uteluft, Kd | SF,Kd = Wärmesumme, Fortluft - Außenluft, Kd | SJ,Kd = współczynnik przenikania ciepła między powietrzem a temperaturą powietrza zewnętrznego, Kd | SJ,Kd = heitõhu ja välisõhu temperatuuri vaheline soojusvajadusarv, Kd | SJ,Kd = piesārņotā un āra gaisa temperatūras savstarpējais nepieciešamā siltuma koeficients, Kd | SJ, Kd = šilumos poreikio tarp išeinančio ir lauko oro temperatūros koeficientas, Kd
|  | 104 | Vesikiertoisen lämmityspatterin mitoitus | Dimensioning of heating coil | Dimensionering av vattenburet värmebatteri | Dimensionierung von Heizregistern | Dobór nagrzewnicy wodnej | Vesiringlusega kalorifeeri arvutus | Ūdens cirkulācijas apsildes radiatora dimensionēšana | Radiatoriaus su vandens cirkuliacija matmenys
|  | 105 | Ei käytettävissä tässä mallissa | Not available for selected model | Ej tillgänglig för denna modell | Für das ausgewählte Modell nicht verfügbar | Niedostępne w tym modelu | Ei ole selle mudeli puhul kasutatav | Šim modelim nav izmantojams | Šiame modelyje nėra
|  | 106 | Syötä mitoitus- ja tavoitearvot: | Insert parameters: | Fyll i dimensionerings- och målvärden: | Parameter einfügen: | Wprowadź rozmiar i wartości docelowe: | Sisesta arvutus- ja sihtväärtused: | Ievadīt dimensionēšanas un mērķa vērtības: | Įveskite matmenis ir tikslines vertes:
|  | 107 | Aloita syöttämällä joko meno- tai paluuveden lämpötila | Start by inserting either inlet or outlet water temperature | Börja med att fylla i temperatur för tillopps- eller returvatten | Beginnen Sie mit der Eingabe entweder der Einlass- oder der Auslasswassertemperatur | Rozpocznij od wprowadzenia temperatury wody zasilającej lub powrotnej | Alustuseks sisesta kas välja- või tagasivooluvee temperatuur | Sākt ievadi, ievadot turpgaitas vai atpakaļgaitas ūdens temperatūru | Pirmiausia įveskite įleidžiamo arba grįžtančio vandens temperatūrą
|  | 108 | Patterille tulevan ilman lämpötila | Inlet air temperature | Lufttemperatur vid batteriingång | Einlasslufttemperatur | Temperatura powietrza na wejściu | Kalorifeeri siseneva õhu temperatuur | Pie radiatora pieplūstošā gaisa temperatūra | Į radiatorių įeinančio oro temperatūra
|  | 109 | Patterilta lähtevän ilman lämpötila | Outlet air temperature | Lufttemperatur vid batteriutgång | Auslasslufttemperatur | Temperatura powietrza na wyjściu | Kalorifeerist väljuva õhu temperatuur | No radiatora aizplūstošā gaisa temperatūra | Iš radiatoriaus išeinančio oro temperatūra
|  | 110 | Menoveden lämpötila | Inlet water temperature | Temperatur för tilloppsvatten | Wassereinlasstemperatur | Temperatura wody zasilającej | Väljuva vee temperatuur | Turpgaitas ūdens temperatūra | Įleidžiamo vandens temperatūra
|  | 111 | Paluuveden lämpötila | Outlet water temperature | Temperatur för returvatten | Wasserauslasstemperatur | Temperatura wody powrotnej | Tagasivooluvee temperatuur | Atpakaļgaitas ūdens temperatūra | Grįžtančio vandens temperatūra
|  | 112 | Tuloilman tilavuusvirta | Supply air volume flow | Tilluftens volymflöde | Zuluftvolumenstrom | Przepływ objętościowy powietrza nawiewanego | Sissepuhkeõhu vooluhulk | Ieplūstošā gaisa tilpuma plūsma | Tiekiamo oro srautas
|  | 113 | Tarvittava lämmitysteho: | Required heating power | Värmeeffektbehov | Erforderliche Heizleistung | Wymagana moc grzewcza: | Vajalik küttevõimsus: | Nepieciešamā apsildes jauda: | Reikalinga šildymo galia:
|  | 114 | * Käytettäessä Oras DN15S suurtehorunkoa + Stabila -patteriventtiiliä (täysin auki, KV = 1,00) | *Using Oras DN15S Radiator valve body & Stabila radiator valve (fully open, CV = 1.00) | * Vid användning av Oras DN15S radiatorventilshus + Stabila radiatorventil (fullt öppen, CV = 1,00) | Bei Verwendung von Oras DN15S + Stabila -Heizkörperventil (vollständig geöffnet, CV = 1.00) | * W przypadku korzystania z korpusu o dużej pojemności Oras DN15S + zaworu grzejnikowego Stabila (całkowicie otwarty, KV = 1,00) | * Kasutades Oras DN15S suurt korpust + Stabila kalorifeeri ventiili (täielikult avatud, KV = 1,00) | * Izmantojot Oras DN15S lieljaudas korpusu + Stabila radiatora ventili (pilnīgi atvērtu, KV = 1,00) | * Naudojant didelės galios „Oras DN15S“ korpusą + „Stabila“ radiatoriaus vožtuvą (visiškai atidarytas, KV = 1,00)
|  | 115 | Patterimitoitus menoveden lämpötilan mukaan | Heating coil dimensioning by inlet water temperature | Batteridimensionering baserat på temperatur för tilloppsvatten | Dimensionierung entsprechend der Einlasswassertemperatur | Dobór nagrzewnicy w zależności od temperatury wody zasilającej | Kalorifeeri arvutus vastavalt väljuva vee temperatuurile | Radiatoru dimensionēšana atbilstoši turpgaitas ūdens temperatūrai | Radiatoriaus matmenys pagal įleidžiamo vandens temperatūrą
|  | 116 | Patterimitoitus paluuveden lämpötilan mukaan | Heating coil dimensioning by outlet water temperature | Batteridimensionering baserat på temperatur för returvatten | Dimensionierung entsprechend der Auslasswassertemperatur | Dobór nagrzewnicy w zależności od temperatury wody powrotnej | Kalorifeeri arvutus vastavalt tagasivooluvee temperatuurile | Radiatoru dimensionēšana atbilstoši atpakaļgaitas ūdens temperatūrai | Radiatoriaus matmenys pagal grįžtančio vandens temperatūrą
|  | 117 | Menoveden lämpötila | Inlet water temperature | Temperatur för tilloppsvatten | Einlasswassertemperatur | Temperatura wody zasilającej | Väljuva vee temperatuur | Turpgaitas ūdens temperatūra | Įleidžiamo vandens temperatūra
|  | 118 | Paluuveden lämpötila | Outlet water temperature | Temperatur för returvatten | Auslasswassertemperatur | Temperatura wody powrotnej | Tagasivooluvee temperatuur | Atpakaļgaitas ūdens temperatūra | Grįžtančio vandens temperatūra
|  | 119 | Virtaama | Volume flow | Volymflöde | Volumenstrom | Natężenie przepływu | Vooluhulk | Plūsma | Srautas
|  | 120 | Patterin nestepuolen painehäviö | Heating coil fluid side pressure loss | Tryckfall för vätskesidan av värmebatteri | Flüssigkeitsseitiger Druckabfall der Heizregister | Spadek ciśnienia po stronie cieczy w nagrzewnicy | Kalorifeeri vedelikupoole rõhukadu | Radiatora šķidruma spiediena zudums | Radiatoriaus skysčio slėgio sumažėjimas
|  | 121 | Säätöventtiilin painehäviö* | Control valve pressure loss* | Tryckfall för reglerventil* | Druckverlust des Regelventils* | Spadek ciśnienia na zaworze sterującym* | Reguleerventiili rõhukadu* | Regulācijas ventiļa spiediena zudums* | Slėgio sumažėjimas valdymo vožtuve*
|  | 122 | Virtausnopeus | Flow velocity | Flödeshastighet | Fliessgeschwindigkeit | Prędkość przepływu | Voolukiirus | Plūsmas ātrums | Srauto greitis
|  | 123 | Pistotulppa 230 V, 50 Hz, 10 A, max 1100 W | Electric plug 230 V, 50 Hz, 10 A, max 1100 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1100 W | Stecker 230 V, 50 Hz, 10 A, max 1100 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1100 W | Pistik 230 V, 50 Hz, 10 A, max 1100 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1100 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1100 W
|  | 124 | Sähkönsyöttö: | Power supply: | Strömförsörjning: | Stromversorgung: | Zasilanie elektryczne: | Elektritoide: | Elektrības padeve: | Elektros tiekimas:
|  | 125 | käytettäessä 'dB-pakettia' (Huom! Vaatii kaappirungon) | using 'dB-paketti' (NB! Requires a cabinet) | Vid använding av 'dB-paketti' (Obs! Kräver en skåpram) | mit Schallgedämmtes Gehäuse "dB-paketti" (N.B. Braucht einen Schrankrahmen) | podczas korzystania z "pakietu dB" (Uwaga! Wymaga ramy szafki) | kasutades 'dB-paketti' (NB! Nõuab kapiraami) | izmantojot 'dB-paketi' (Uzmanību! Nepieciešams skapja korpuss) | naudojant „dB paketą“ (Dėmesio! Reikalingas rėminis korpusas)
|  | 126 | Valitse laitemallin yhteydessä vesikiertoinen lämmityspatteri | Select heating coil in the model selection menu | Välj värmebatteri vid val av modell | Wasser-Heizregister im Modellauswahlmenü auswählen | Wybierz chłodnicę chłodzoną wodą dla swojego modelu | Vali seadmemudeli puhul vesiringlusega kalorifeer | Kopā ar iekārtas modeli izvēlieties ūdens cirkulācijas radiatoru | Rinkdamiesi įrangos modelį, pasirinkite šildymo radiatorių su vandens cirkuliacija
|  | 127 | Ei käyttöalueella. Tarkista mitoitusarvot. | Value out of range. Check parameters. | Ej på användningsområdet. Kontrollera dimensioneringsvärden. | Wert außerhalb des Verwendungsbereichs. Parameter prüfen. | Nie w obszarze użytkowania. Sprawdź wartości wymiarowe | Pole kasutusalas. Kontrolli arvutusväärtusi. | Nav ekspluatācijas diapazonā. Pārbaudīt dimensionēšanas vērtības. | Naudojimo zonoje nėra. Patikrinkite matmenų vertes.
|  | 128 | Äänenvaimennuskotelo ei käytettävissä tässä mallissa | Sound insulated casing not available for selected model | Ljudisolerat hölje ej tillgängligt för denna modell. | Schallgedämmtes Gehäuse für ausgewähltes Modell nicht verfügbar | Obudowa z redukcją szumów nie jest dostępna dla tego modelu | Mürasummutuskate ei ole selle mudeli puhul kasutatav | Skaņu slāpējošs korpuss šim modelim nav pieejams | Garso slopinimo gaubto šiame modelyje nėra
|  | 129 | * Huom. keittiöohitusta käytettäessä kokonaispoistoilmavirta syötettyä mitoitusarvoa suurempi | * With kitchen bypass, the total extract air volume flow is larger than the inserted value | * Vid användning av förbigång för kök är totala frånluftsvolymflödet större än det insatta dimensioneringsvärdet. | * Bei Küchen-bypass ist der Gesamtabluftvolumenstrom größer als der eingegebene Wert | * Uwaga: W przypadku korzystania z okapu kuchennego całkowity przepływ powietrza wylotowego jest wyższy niż wartość znamionowa wejścia. | * NB! Köögi möödavoolu kasutamisel on väljatõmbeõhu õhuvoolu väärtus sisestatud arvutusväärtusest suurem | * Uzmanību: ja tiek apieta virtuve, kopējā izplūstošā gaisa plūsma ir lielāka par ievadīto dimensionēšanas vērtību | * Pastaba: naudojant virtuvės apylanką, bendras ištraukiamo oro srautas yra didesnis už įvestą išmatuotą vertę.
|  | 130 | Säävyöhyke (valtio/maa) | Climate zone (state/country) | Klimatzon (stat/land) | Klimazone (Staat/Land) | Strefa klimatyczna (kraj) | Kliimavöönd (riik/maa) | Meteoroloģiskā zona (valsts/teritorija) | Klimato juosta (valstybė / šalis)
|  | 131 | Säävyöhyke (kunta/kaupunki) | Climate zone (municipality/city) | Klimatzon (kommun/stad) | Klimazone (Gemeinde/Stadt) | Strefa klimatyczna (gmina/miasto) | Kliimavöönd (vald/linn) | Meteoroloģiskā zona (pašvaldība/pilsēta) | Klimato juosta (savivaldybė / miestas)
|  | 132 | Ilman tilavuusvirta [m³/h] | Air volume flow [m³/h] | Luftens volymflöde [m³/h] | Luftvolumenstrom [m³/h] | Natężenie przepływu powietrza [m³/h] | Õhu vooluhulk [m³/h] | Gaisa tilpuma plūsma [m³/h] | Oro srautas [m³/h]
|  | 133 | Mitoituspiste (syötä tilavuusvirta ja paine-ero) | Operating point (insert air flow and pressure difference values): | Driftpunkt (ange luftflöde och tryckdifferensvärden): | Betriebspunkt (Geben Sie Luftvolumenstrom- und Druckdifferenzwerte ein): | Punkt wymiarowania (wprowadź przepływ objętościowy i różnicę ciśnień) | Arvutuspunkt (sisesta vooluhulk ja rõhuerinevus) | Dimensionēšanas punkts (ievadīt tilpuma plūsmu un spiediena starpību) | Matavimo taškas (įveskite srautą ir slėgio skirtumą)
|  | 134 | Tehostustilanteen laskenta: | Boost situation calculation: | Beräkning av forceringssituation: | Berechnung der Verstärkungssituation: | Obliczenie zapasu wydajności jednostki: | Võimendusolukorra arvutamine: | Efektivitātes palielināšanas situācijas aprēķins: | Galingumo didinimo apskaičiavimas:
|  | 135 | Maksimi tehostusvara: | Maximum boost reserve: | Maximal forceringsreserv: | Maximale Verstärkungsreserve: | Maksymalny zapas wydajności: | Maksimaalne võimendusvaru: | Maksimālā efektivitātes palielināšana: | Didžiausias galingumo padidinimas:
|  | 136 | Syötä haluttu tehostusarvo: | Insert the desired boost value: | Ange forceringsvärde: | Verstärkungswert eingeben: | Wprowadź żądaną wartość zapasu wydajności: | Sisesta soovitud võimendusväärtus: | Ievadīt vēlamo efektivitātes palielināšanas vērtību: | Įveskite norimą galingumo padidinimo vertę:
|  | 137 | Tehostusarvo [%]: | Boost value [%]: | Forceringsvärde [%]: | Verstärkungswert [%]: | Wartość zapasu wydajności [%]: | Võimendusväärtus [%]: | Efektivitātes palielināšanas vērtība [%]: | Galingumo padidinimo vertė [%]:
|  | 138 | Toimintapiste tehostustilanteessa: | Operating point in boost situation: | Driftpunkt i forceringssituation: | Betriebspunkt in der Verstärkungssituation: | Punkt pracy w przypadku użycia programu TURBO: | Toimimiskoht võimendusolukorras: | Darbības punkts efektivitātes palielināšanas situācijā: | Veikimo taškas galingumo padidinimo atveju:
|  | 139 | Määritettyä tehostusarvoa ei saavutettu | The specified boost value was not achieved | Det angivna forceringsvärdet uppnåddes inte | Der festgelegte Verstärkungswert wurde nicht erreicht | Zdefiniowana wartość wydajności nie została osiągnięta | Määratud võimendusväärtust ei saavutatud | Noteiktā efektivitātes palielināšanas vērtība nav sasniegta | Nustatyta galingumo padidinimo vertė nebuvo pasiekta
|  | 140 | Laskenta YM:n Monisteen 122 mukaisesti |  |  |  | Obliczenia zgodnie z Publikacją Ministerstwa Środowiska YM 122 | Arvutamine YM-i trükise 122 kohaselt | Aprēķins saskaņā ar Vides ministrijas kopiju Nr. 122 | Skaičiavimas pagal Aplinkos ministerijos leidinį Nr. 122
|  | 141 | Sovelletut asiakirjat ja standardit: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Tasauslaskentaopas 2018, YM moniste 122 ja Komission asetukset (EU) N:o 1253/2014 & N:o 1254/2014. Emme vastaa ohjelman mahdollisista virheistä tai niiden aiheuttamista välittömistä tai välillisistä virheistä. | Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program. | Tillämpade dokument och standarder: SFS-EN 13141-7, LVI 30-10529, Finska Miljöministeriets förordning 1009/2017, samt kommisionens förordningar (EU) nr 1253//2014 & nr 1254/2014. Vi ansvarar inte för direkt eller indirekt skada orsakad av möjliga fel i produktvalprogrammet. | Angewandte Dokumente und Normen: SFS-EN 13141-7, LVI 30-10529, Finnisches Umweltministerium: Dekret 1009/2017 und Verordnung (EU) Nr. 1253/2014 & 1254/2014 Der Kommission. Wir sind nicht verantwortlich für direkte oder indirekte Schäden, die durch mögliche Fehler im Auswahlprogramm verursacht werden. | Obowiązujące dokumenty i normy: SFS-EN 13141-7, LVI 30-10529, Rozporządzenie Ministerstwa Środowiska YMa1009/2017, Przewodnik bilansowania 2018, Publikacja Ministerstwa Środowiska YM 122 oraz rozporządzenia Komisji (UE) nr 1253/2014 i nr 1254/2014. Nie ponosimy odpowiedzialności za jakiekolwiek błędy w programie ani za jakiekolwiek bezpośrednie lub pośrednie błędy przez nie spowodowane. | Kohaldatud dokumendid ja standardid: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Ühtlustamisarvutuste juhend 2018, YM paljundus 122 ja Komisjoni määrused (EL) nr 1253/2014 ja nr 1254/2014. Me ei vastuta tarkvara võimalike puuduste ega nendest tulenevate otseste või kaudsete vigade eest. | Izmantotie dokumenti un standarti: SFS-EN 13141-7, LVI 30-10529, Vides ministrijas dekrēts 1009/2017, Balansēšanas aprēķina rokasgrāmata 2018, Vides ministrijas kopija Nr. 122 un Komisijas Regulas (ES) Nr. 1253/2014 un Nr. 1254/2014. Nenesam atbildību par iespējamām kļūdām programmā vai to izraisītām tiešām vai netiešām kļūdām. | Taikyti dokumentai ir standartai: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, 2018 m. skaičiavimo vadovas, Aplinkos ministerijos leidinys 122 ir Komisijos reglamentai (ES) Nr. 1253/2014 ir Nr. 1254/2014. Neatsakome už jokias programos klaidas ar dėl jų atsiradusias tiesiogines ar netiesiogines paklaidas.
|  | 142 | Valitse säävyöhyke (kaupunki) | Select climate zone (city) | Välj klimatzon (kommun/stad) | Wählen Sie die klimazone (Stadt) | Wybierz strefę klimatyczną (miasto) | Kliimavööndi valimine (linn) | Izvēlēties meteoroloģisko zonu (pilsēta) | Pasirinkite klimato juostą (miestas)
|  | 143 | Huom. yllä olevat arvot sisältävät myös laitteen elektroniikan. | Note: The above values also include the device's electronics. | De ovanstående värdena inkluderar också enhetens elektronik. | Die obigen Werte beinhalten auch die Elektronik des Geräts. | Uwaga: Powyższe wartości obejmują również zużycie energii przez elektronikę urządzenia. | NB! Ülaltoodud väärtused hõlmavad ka seadme elektroonikat. | Uzmanību: iepriekš minētās vērtības ietver arī iekārtas elektroniku. | Pastaba: į pirmiau nurodytas vertes įskaičiuota ir prietaiso elektronika.
|  | 144 | Lämmöntalteenottokennon hyötysuhde (EN 308) | Heat recovery cell efficiency (EN 308) | Verkningsgrad för värmeåtervinningscell (EN 308) | Wirkungsgrad der Wärmerückgewinnungszelle (EN 308) | Sprawność wymiennika odzysku ciepła (EN 308) | Soojusvaheti kasutegur (EN 308) | Rekuperatora elementa lietderības koeficients (EN 308) | Šilumos atgavimo elemento efektyvumo koeficientas (EN 308)
|  | 145 | Puhaltimien ja elektroniikan sähkönkulutus | Electricity consumption of fans and electronics | Elkonsumtion för fläktar och elektronik | Stromverbrauch von Ventilatoren und Elektronik | Zużycie energii elektrycznej przez wentylatory i elektronikę | Ventilaatorite ja elektroonika voolutarve | Ventilatora un elektronikas strāvas patēriņš | Ventiliatorių ir elektronikos įtaisų elektros sąnaudos
|  | 146 | Tuloilman lämpötilan rajoitus | Supply air temperature limitation | Begränsning av tilluftstemperatur | Begrenzung der Zulufttemperatur | Ograniczenie temperatury powietrza nawiewanego | Sissepuhkeõhu temperatuuri piirang | Ieplūstošā gaisa temperatūras ierobežojums | Tiekiamo oro temperatūros apribojimas
|  | 147 | Rajoitettu | Limited | Begränsad | Begrenzt | Ograniczone | Piiratud | Ierobežots | Apribota
|  | 148 | Ei rajoitusta | No limitation | Ingen begränsning | Keine Begrenzung | Brak ograniczenia | Piiranguteta | Neierobežots | Neribojama
|  | 149 | Tuloilman tavoitelämpötila | Target supply air temperature | Målinställd temperatur för tilluften | Ziel-Zulufttemperatur | Docelowa temperatura powietrza nawiewanego | Sissepuhkeõhu soovitud temperatuur | Ieplūstošā gaisa mērķa temperatūra | Pageidaujama tiekiamo oro temperatūra
|  | 150 | Mitoittava ulkoilman minimilämpötila | Design minimum outdoor air temperature | Dimensionerande utomhustemperatur | Auslegungsmindestaußentemperatur | Minimalna mierzalna temperatura powietrza zewnętrznego | Arvutatav minimaalne välisõhu temperatuur | Dimensionēšanas minimālā āra gaisa temperatūra | Mažiausia išmatuojama lauko oro temperatūra
|  | 151 | Tarvittava jälkilämmityspatterin ottoteho | Required reheating power | Utgångseffekt för eftervärmningsbatteriet | Abgabeleistung des Nachheizregisters | Wymagana moc wejściowa wymiennika dogrzewania wtórnego | Vajalik järelküttekalorifeeri võimsusvajadus | Nepieciešamā pēcapsildes radiatora ieejas jauda | Reikiama pašildymo radiatoriaus įsiurbimo galia
|  | 152 | Jälkilämmityspatterin maksimiteho | Maximum power of the reheater | Maximal effekt för eftervärmningsbatteriet | Maximalleistung des Nachheizregisters | Maksymalna moc wymiennika dogrzewania wtórnego | Järelsoojenduskalorifeeri maksimaalne võimsus | Pēcapsildes radiatora maksimālā jauda | Didžiausia pašildymo radiatoriaus galia
|  | 153 | h / vrk | h / day | h / d | h / d | h / d | h / d | h / d | h / d
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176

## KirjastoC (hidden)
Versio | 7.3 | [5 empty] | Korjattu Airfi:lta 25.9.2024 saadun kommenttiexcelin perusteella (37/152 korjattua --> 25% pielessä)
| Kielivalinta: |  | 1. SUOMI | 2. ENGLANTI | 3. RUOTSI | 4. SAKSA | 5. PUOLA | 6. VIRO | 7. LATVIA | 8. LIETTUA | Taulukot: | Tulostusvälilehden ohjauksia, jos kielivalinta suomi
| 2 | 1 | Versio 7.3 | Version 7.3 | Version 7.3 | Version 7.3 | Wersja 7.3 | Versioon 7.3 | Versija 7.3 | 7.3 versija
|  | 2 | Airfi: C-sarjan ilmanvaihtokoneen valintaohjelma | Airfi: C series air handling unit selection program | Airfi: produktvalprogram för ventilationsaggregat | Airfi: Auswahlprogramm für Lüftungsgeräte | Airfi: program doborowy urządzeń wentylacyjnych | Airfi: ventilatsiooniseadme valimise tarkvara | Airfi: ventilācijas iekārtas izvēles programma | Airfi: vėdinimo įrangos parinkties programa | Pressure difference [Pa] | Suomi valittu | FALSE
|  | 3 | Kohde: | Project: | Projekt: | Projekt: | Obiekt: | Objekt: | Objekts: | Objektas: | Air volume flow [dm³/s] | Suomi ei valittu | TRUE
|  | 4 | Suunnittelija: | Name: | Namn: | Designer: | Projektant: | Projekteerija: | Projektētājs: | Projektuotojas: | Air volume flow [m³/h]
|  | 5 | Valitse malli erillisellä välilehdellä | Selected model: | Vald modell: | Ausgewähltes Modell: | Wybrany model: | Valitud mudel: | Izvēlētais modelis: | Pasirinktas modelis: | Supply air temperature after heat exchanger
|  | 6 | Äänenvaimennuskotelo: 'dB-paketti' (Huom! Vaatii kaappirungon) | Sound insulated casing: "dB-paketti" (NB! Requires a cabinet) | Ljudisolerat hölje: "dB-paketti" (Obs! Kräver en skåpram) | Schallgedämmtes Gehäuse: "dB-paketti" (N.B. Braucht einen Schrankrahmen) | Obudowa tłumiąca dźwięk: "pakiet dB" (Uwaga! Wymaga ramy szafki) | Mürasummutuskate: 'dB-pakett' (NB! Nõuab kapiraami) | Skaņu slāpējošs korpuss: 'dB-pakete' (Uzmanību! Nepieciešams skapja korpuss) | Garso slopinimo gaubtas: „dB paketas“ (Dėmesio! Reikalingas rėminis korpusas) | Supply air temperature [°C]
|  | 7 | Vesikiertoinen lämmityspatteri | Heating coil | Värmebatteri | Wasser-Heizregister | Nagrzewnica wodna | Veeringlusega kalorifeer | Ūdens cirkulācijas apsildes radiators | Šildymo radiatorius su vandens cirkuliacija | Outdoor air temperature [°C]
|  | 8 | Ei käytettävissä tässä mallissa | Not available for the selected model | Ej tillgänglig för denna modell | Für das ausgewählte Modell nicht verfügbar | Niedostępne w tym modelu | Ei ole selle mudeli puhul kasutatav | Šim modelim nav izmantojams | Šiame modelyje nėra
|  | 9 | Pistotulppa 230 V, 50 Hz, 10 A, max 1165 W | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1165 W | Stecker 230 V, 50 Hz, 10 A, max 1165 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1165 W | Pistik 230 V, 50 Hz, 10 A, max 1165 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1165 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1165 W | Exhaust air temperature
|  | 10 | Pistotulppa 230 V, 50 Hz, 10 A, max 1165 W | Electric plug 230 V, 50 Hz, 10 A, max 1165 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1165 W | Stecker 230 V, 50 Hz, 10 A, max 1165 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1165 W | Pistik 230 V, 50 Hz, 10 A, max 1165 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1165 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1165 W | Exhaust air temperature [°C]
|  | 11 | Pistotulppa 230 V, 50 Hz, 16 A, max 2200 W | Electric plug 230 V, 50 Hz, 16 A, max 2200 W | Stickkontakt 230 V, 50 Hz, 16 A, max 2200 W | Stecker 230 V, 50 Hz, 16 A, max 2200 W | Wtyczka 230 V, 50 Hz, 16 A, maks. 2200 W | Pistik 230 V, 50 Hz, 16 A, max 2200 W | Kontaktspraudnis 230 V, 50 Hz, 16 A, maks. 2200 W | Kištukas 230 V, 50 Hz, 16 A, maks. 2200 W | Outdoor air temperature [°C]
|  | 12 | Pistotulppa 230 V, 50 Hz, 16 A, max 3500 W | Electric plug 230 V, 50 Hz, 16 A, max 3500 W | Stickkontakt 230 V, 50 Hz, 16 A, max 3500 W | Stecker 230 V, 50 Hz, 16 A, max 3500 W | Wtyczka 230 V, 50 Hz, 16 A, maks. 3500 W | Pistik 230 V, 50 Hz, 16 A, max 3500 W | Kontaktspraudnis 230 V, 50 Hz, 16 A, maks. 3500 W | Kištukas 230 V, 50 Hz, 16 A, maks. 3500 W
|  | 13 | Pistotulppa 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Electric plug 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Stickkontakt 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Stecker 400 VAC, 50 Hz, 3 x 16 A, max 8250 W | Wtyczka 400 VAC, 50 Hz, 3 x 16 A, maks. 8250 W | Pistik 400 V AC, 50 Hz, 3 x 16 A, max 8250 W | Kontaktspraudnis 400 VAC, 50 Hz, 3 x 16 A, maks. 8250 W | Kištukas 400 VAC, 50 Hz, 3 x 16 A, maks. 8250 W | Air density: 1.2 kg/m³
|  | 14 | Pistotulppa 230 V, 50 Hz, 10 A, max 1255 W | Electric plug 230 V, 50 Hz, 10 A, max 1255 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1255 W | Stecker 230 V, 50 Hz, 10 A, max 1255 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1255 W | Pistik 230 V, 50 Hz, 10 A, max 1255 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1255 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1255 W | Supply air
|  | 15 | Ilman tiheys: 1,2 kg/m³ | Air density: 1.2 kg/m³ | Lufttäthet: 1,2 kg/m³ | Luftdichte: 1,2 kg/m³ | Gęstość powietrza: 1,2 kg/m³ | Õhu tihedus: 1,2 kg/m³ | Gaisa blīvums: 1,2 kg/m³ | Oro tankis: 1,2 kg/m³ | Extract air
|  | 16 | Tuloilma | Supply air | Tilluft | Zuluft | Powietrze nawiewane | Sissepuhkeõhk | Ieplūstošais gaiss | Tiekiamas oras
|  | 17 | Poistoilma | Extract air | Frånluft | Abluft | Powietrze wywiewane | Väljatõmbeõhk | Izplūstošais gaiss | Ištraukiamas oras | Sound insulated casing: "dB-paketti" (NB! Requires a cabinet)
|  | 18 | Paine-ero [Pa] | Pressure difference [Pa] | Tryckskillnad [Pa] | Druckdifferenz [Pa] | Różnica ciśnień [Pa] | Rõhuerinevus [Pa] | Spiedienu starpība [Pa] | Slėgio skirtumas [Pa] | Heating coil
|  | 19 | Ilman tilavuusvirta [dm³/s] | Air volume flow [dm³/s] | Luftens volymflöde [dm³/s] | Luftvolumenstrom [dm³/s] | Natężenie przepływu powietrza [dm³/s] | Õhu vooluhulk [dm³/s] | Gaisa tilpuma plūsma [dm³/s] | Oro srautas [dm³/s]
|  | 20 | Tuloilma (syötä arvot): | Supply air (insert values): | Tilluft (fyll i värden): | Zuluft (Werte eingeben): | Nawiewane powietrze (wprowadzić wartości): | Sissepuhkeõhk (sisesta väärtused): | Ieplūstošais gaiss (ievadīt vērtības): | Tiekiamas oras (įveskite vertes):
|  | 21 | Ilman tilavuusvirta: | Air volume flow: | Luftens volymflöde: | Luftvolumenstrom: | Natężenie przepływu powietrza | Õhu vooluhulk: | Gaisa tilpuma plūsma: | Oro srautas:
|  | 22 | Paine-ero: | Pressure difference: | Tryckskillnad: | Druckdifferenz [Pa] | Różnica ciśnień: | Rõhuerinevus | Spiedienu starpība: | Slėgio skirtumas:
|  | 23 | Ei käyttöalueella | Value out of range | Värde utanför området | Werte überprüfen | Nie w obszarze użytkowania | Pole kasutusalas | Nav ekspluatācijas diapazonā | Naudojimo zonoje nėra
|  | 24 | Poistoilma (syötä arvot): | Extract air (insert values): | Frånluft (fyll i värden): | Abluft (Werte eingeben): | Powietrze wylotowe (wprowadzić wartości): | Väljatõmbeõhk (sisestage väärtused): | Izplūstošais gaiss (ievadīt vērtības): | Ištraukiamas oras (įveskite vertes):
|  | 25 | Tulopuhallin: | Supply fan: | Tilluftsfläkt: | Zuluftsventilator: | Wentylator nawiewny: | Sissepuhkeventilaator: | Ieplūstošā gaisa ventilators: | Įsiurbimo ventiliatorius:
|  | 26 | Ohjausjännite: | Control voltage: | Styrspänning: | Steuerspannung: | Napięcie sterowania: | Juhtpinge: | Vadības spriegums: | Valdymo įtampa:
|  | 27 | Puhaltimen ottoteho: | Fan power: | Fläktens ineffekt: | Eingangsleistung: | Moc wentylatora: | Ventilaatori võimsustarve: | Ventilatoru ieejas jauda: | Ventiliatorių įsiurbimo galia:
|  | 28 | Poistopuhallin: | Extract fan: | Frånluftsfläkt: | Abluftsventilator: | Wentylator wyciągowy: | Väljatõmbeventilaator: | Izplūstošā gaisa ventilators: | Ištraukiamasis ventiliatorius:
|  | 29 | Kokonaisteho: | Total power: | Totaleffekt: | Gesamtleistung: | Całkowita moc: | Koguvõimsus: | Kopējā jauda: | Bendra galia:
|  | 30 | SFP: | SFP: | SFP: | SFP: | SFP: | SFP: | SFP: | SFP:
|  | 31 | Äänitehotasot liitäntäkanavissa | Sound power levels in connection ducts | Ljudeffektnivåer i kanalmynningarna | Schallleistungspegel in Anschlusskanäle | Poziomy mocy akustycznej w kanałach przyłączeniowych | Helivõimsustasemed ühenduskanalites | Skaņas jaudas līmeņi savienotājkanālos | Garso galios lygis jungiamajame kanale
|  | 32 | Liitäntäkanava | Connection duct | Kanalmynning | Anschlusskanal | Kanał przyłączeniowy | Ühenduskanal | Pieslēguma kanāli | Jungiamasis kanalas
|  | 33 | Tuloilma | Supply air | Tilluft | Zuluft | Nawiew | Sissepuhkeõhk | Ieplūstošais gaiss | Tiekiamas oras
|  | 34 | Ulkoilma | Outdoor air | Uteluft | Außenluft | Czerpnia | Välisõhk | Āra gaiss | Lauko oras
|  | 35 | Poistoilma | Extract air | Frånluft | Abluft | Wywiew | Väljatõmbeõhk | Izplūstošais gaiss | Ištraukiamas oras
|  | 36 | Jäteilma | Exhaust air | Avluft | Fortluft | Wyrzutnia | Heitõhk | Piesārņotais gaiss | Išeinantis oras
|  | 37 | Keittiöohitus | Kitchen bypass | Förbigång för kök | Küchen Bypass | Bypass okapu kuchennego | Köögi möödaviik | Virtuves apeja | Virtuvės aplenkimas
|  | 38 | Äänitehotasot oktaavikaistoittain LW,okt [dB] | Sound power levels in octave bands LW,oct [dB] | Ljudeffektnivåer i oktavband LW,okt [dB] | Schallleistungspegel in Oktavbändern LW,okt [dB] | Poziomy mocy akustycznej w paśmie oktawowym LW,oct [dB] | Helivõimsuse tasemed oktaaviribade kaupa LW,okt [dB] | Skaņas jaudas līmeņi pa oktāvas joslām LW,okt [dB] | Garso galios lygiai pagal oktavų juostas LW,okt [dB]
|  | 39 | LWtot | LWtot | LWtot | LWtot | LWtot | LWtot | LWtot | LWtot
|  | 40 | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot | LWAtot
|  | 41 | Äänitehotasot ympäristöön | Sound power levels through casing: | Ljudeffektnivå till omgivningen | Schallleistungspegel durch das Gehäuse | Poziom mocy akustycznej generowany do otoczenia | Helivõimsuse tasemed keskkonnas | Skaņas jaudas līmeņi vidē | Garso galios lygiai aplinkoje
|  | 42 | Vaipan läpi | Through casing | Genom manteln | Durch das Gehäuse | Przez obudowę | Läbi katte | Caur apvalku | Per vožtuvą
|  | 43 | Äänipainetaso huonetilassa, jonka ääniabsorptioala 10m²: | Sound pressure level in a room with an absorption area of 10m²: | Ljudtrycksnivå i ett rum, vars ljudabsorptionsarea är 10m²: | Schalldruckpegel im Raum mit einer Absorptionsfläche von 10m² | Poziom ciśnienia akustycznego w pomieszczeniu o powierzchni pochłaniania dźwięku wynoszącej 10 m²: | Helirõhutase ruumis, mille heli neeldumispind on 10 m²: | Skaņas spiediena līmenis telpā, kuras skaņas absorbcijas platība ir 10 m²: | Garso slėgio lygis patalpoje, kurios garso sugerties plotas yra 10 m²:
|  | 44 | Äänipainetaso tyypillisessä kylpyhuoneessa tai tekn. tilassa (V < 10 m³), jonka ääniabsorptioala < 2-3 m²: | Sound pressure level in a typical bathroom (V < 10 m³) with an absorption area < 2-3 m²: | Ljudtrycksnivå i ett typiskt badrum (V < 10 m³), vars ljudabsorptionsarea är < 2-3 m² | Schalldruckpegel in typischem Badezimmer (V < 10 m³) mit einer Absorptionsfläche < 2-3 m²: | Poziom ciśnienia akustycznego w typowej łazience lub pomieszczeniu technicznym (V < 10 m³) o powierzchni pochłaniania dźwięku < 2-3 m²: | Helirõhutase tüüpilises vannitoas või tehnoruumis (V < 10 m³), mille heli neeldumispind on < 2-3 m²: | Skaņas spiediena līmenis tipiskā vannas istabā vai tehniskajā telpā (V < 10 m³), kuras skaņas absorbcijas platība ir < 2-3 m²: | Garso slėgio lygis įprastame vonios kambaryje arba techninėje patalpoje (V < 10 m³), kurios garso sugerties plotas < 2-3 m²:
|  | 45 | Ominaisenergiankulutus (SEC) ja luokittelu | Specific energy consumption (SEC) and classification | Specifik energianvändning (SEC) och klassifikation | Spezifischer Energieverbrauch (SEV) und Klassifizierung | Jednostkowe zużycie energii (SEC) i klasyfikacja | Spetsiifiline energiatarve (SEC) ja liigitus | Īpatnējais enerģijas patēriņš (Specific Energy Consumption — SEC) un klasifikācija | Savitasis energijos suvartojimas (SEC) ir klasifikacija
|  | 46 | Komission asetusten (EU) N:o 1253/2014 & N:o 1254/2014 mukaisesti | According to Commission Regulations (EU) No 1253/2014 & No 1254/2014 | I enlighet med kommisionens förordningar (EU) nr 1253/2014 & nr 1254/2014 | Entsprechend den Verdordnungen (EU) Nr. 1253/2014 & Nr. 1254/2014 der Kommission | Zgodnie z rozporządzeniami Komisji (UE) nr 1253/2014 i nr 1254/2014 | Vastavalt Euroopa Komisjoni määrustele (EL) nr 1253/2014 ja 1254/2014 | Saskaņā ar Komisijas Regulām (ES) Nr. 1253/2014 un Nr. 1254/2014 | Pagal Komisijos reglamentus (ES) Nr. 1253/2014 ir Nr. 1254/2014
|  | 47 | HUOM! SEC-laskentaa käytetään vain asuinrakennuksiin tarkoitetuilla ilmanvaihtokoneilla. | NB! SEC-calculation is only used for air handling units intended for residential buildings | Obs! SEC-beräkning används endast för ventilationsaggregat avsedda för bostadshus | NB! Die SEV-Berechnung wird nur für Wohnraumlüftungsanlage verwendet | UWAGA! Obliczenia SEC są stosowane tylko w przypadku urządzeń wentylacyjnych przeznaczonych do budynków mieszkalnych. | TÄHELEPANU! SEC arvutust kasutatakse ainult eluhoonetes kasutatavate ventilatsiooniseadmete puhul. | UZMANĪBU! SEC aprēķinu izmanto tikai dzīvojamajām ēkā paredzētajām ventilācijas iekārtām. | DĖMESIO! SEC formulė taikoma tik gyvenamiesiems pastatams skirtiems vėdinimo įrenginiams.
|  | 48 | Vertailuilmavirta: | Reference air flow: | Referensluftflöde: | Nennluftvolumenstrom: | Referencyjny przepływ powietrza: | Võrdlusõhuvool: | References gaisa plūsma: | Lyginamasis oro srautas:
|  | 49 | Laskennan lähtöarvot: | Calculation parameters: | Beräkningsparametrar: | Berechnungsparameter: | Wartości wyjściowe dla obliczeń: | Arvutuse lähteväärtused: | Aprēķinu izejas vērtības: | Skaičiavimo pradinės vertės:
|  | 50 | Yleinen luokittelu | General typology | Allmän klassifiering | Allgemeine Typologie | Klasyfikacja ogólna | Üldine liigitus | Vispārīgā klasifikācija | Bendroji klasifikacija
|  | 51 | Ilmanvaihdon ohjaus | Ventilation control | Ventilationsstyrning | Lüftungssteuerung | Sterowanie wymianą powietrza | Ventilatsiooni juhtimine | Ventilācijas vadība | Vėdinimo valdymas
|  | 52 | Moottori ja ohjaus | Motor & drive | Motor & styrning | Motor und Antrieb | Silnik i układ sterowania | Mootor ja juhtimine | Motors un vadība | Variklis ir valdymas
|  | 53 | Ilmasto | Climate | Klimat | Klima | Klimat | Kliima | Klimats | Klimatas
|  | 54 | Kaikki oikeudet pidätetään. | All rights reserved. | Alla rättigheter förbehållna. | Alle Rechte vorbehalten. | Wszelkie prawa zastrzeżone. | Kõik õigused on kaitstud. | Visas tiesības rezervētas. | Visos teisės saugomos.
|  | 55 | Sovelletut asiakirjat ja standardit: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Tasauslaskentaopas 2018, YM moniste 122 ja Komission asetukset (EU) N:o 1253/2014 & N:o 1254/2014. Emme vastaa ohjelman mahdollisista virheistä tai niiden aiheuttamista välittömistä tai välillisistä virheistä. | Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, "Tasauslaskentaopas 2018" & "Moniste 122", and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program. | Tillämpade dokument och standarder: SFS-EN 13141-7, LVI 30-10529, Finska Miljöministeriets förordning 1009/2017, "Tasauslaskentaopas 2018", Finska Miljöministeriets kompendium 122 samt kommisionens förordningar (EU) nr 1253//2014 & nr 1254/2014. Vi ansvarar inte för direkt eller indirekt skada orsakad av möjliga fel i produktvalprogrammet. | Angewandte Dokumente und Normen: SFS-EN 13141-7, LVI 30-10529, Finnisches Umweltministerium: Dekret 1009/2017, "Tasauslaskentaopas 2018" & "Moniste 122" und Verordnung (EU) Nr. 1253/2014 & 1254/2014 Der Kommission. Wir sind nicht verantwortlich für direkte oder indirekte Schäden, die durch mögliche Fehler im Auswahlprogramm verursacht werden. | Obowiązujące dokumenty i normy: SFS-EN 13141-7, LVI 30-10529, Rozporządzenie Ministerstwa Środowiska YMa1009/2017, Przewodnik bilansowania 2018, Publikacja Ministerstwa Środowiska YM 122 oraz rozporządzenia Komisji (UE) nr 1253/2014 i nr 1254/2014. Nie ponosimy odpowiedzialności za jakiekolwiek błędy w programie ani za jakiekolwiek bezpośrednie lub pośrednie błędy przez nie spowodowane. | Kohaldatud dokumendid ja standardid: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Ühtlustamisarvutuste juhend 2018, YM paljundus 122 ja Komisjoni määrused (EL) nr 1253/2014 ja nr 1254/2014. Me ei vastuta tarkvara võimalike puuduste ega nendest tulenevate otseste või kaudsete vigade eest. | Izmantotie dokumenti un standarti: SFS-EN 13141-7, LVI 30-10529, Vides ministrijas dekrēts 1009/2017, Balansēšanas aprēķina rokasgrāmata 2018, Vides ministrijas kopija Nr. 122 un Komisijas Regulas (ES) Nr. 1253/2014 un Nr. 1254/2014. Nenesam atbildību par iespējamām kļūdām programmā vai to izraisītām tiešām vai netiešām kļūdām. | Taikyti dokumentai ir standartai: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, 2018 m. skaičiavimo vadovas, Aplinkos ministerijos leidinys 122 ir Komisijos reglamentai (ES) Nr. 1253/2014 ir Nr. 1254/2014. Neatsakome už jokias programos klaidas ar dėl jų atsiradusias tiesiogines ar netiesiogines paklaidas.
|  | 56 | Laskentaohjelman laatinut Insinööritoimisto W. Zenner Oy. Laskentaohjelma perustuu SFS-EN 13141-7 mukaisiin laboratoriomittauksiin. | The selection program is made by Zenner Engineers. The program is based on laboratory measurements according to SFS-EN 13141-7. | Produktvalprogrammet har gjorts av Insinööritoimisto W. Zenner Oy. Programmet baserar sig på laboratoriemätningar i enlighet med SFS-EN 13141-7. | Auswahlprogramm ist von Insinööritoimisto W. Zenner Oy erstellt. Das Programm basiert auf Labormessungen nach SFS-EN 13141-7. | Program obliczeniowy został przygotowany przez W. Zenner Oy. Program obliczeniowy oparty jest na pomiarach laboratoryjnych zgodnie z normą SFS-EN 13141-7. | Arvutusprogrammi on koostanud Insinööritoimisto W. Zenner Oy. Arvutusprogramm põhineb standardile SFS-EN 13141-7 vastavatel laboratoorsetel mõõtmistel. | Aprēķinu programmu sagatavoja inženieru birojs Insinööritoimisto W. Zenner Oy. Aprēķinu programmas pamatā ir saskaņā ar SFS-EN 13141-7 veikti laboratorijas mērījumi. | Skaičiavimo programą parengė inžinierių biuras „W. Zenner Oy“. Skaičiavimo programa grindžiama laboratoriniais matavimais pagal SFS-EN 13141-7.
|  | 57 | SEC-luku | SEC-value | SEC-värde | SEV-Wert | Numer SEC | SEC arv | SEC skaitlis | SEC numeris
|  | 58 | Luokka | Class | Klass | Klasse | Klasa | Klass | Klase | Kategorija
|  | 59 | Kanavaliitäntäinen | Ducted units | Kanalansluten enhet | Anlagen mit Kanalanschlußstutzen | Powiązany z kanałem | Kanaliühendusega | Pieslēdzams kanālam | Su jungiamuoju kanalu
|  | 60 | Muu kuin kanavaliitäntäinen | Non-ducted units | Icke kanalansluten enhet | Anlagen ohne Kanalanschlußstutzen | Inne niż powiązane z kanałem | Muu kui kanaliühendusega | Kanālam nepieslēdzams | Su kitokiu, o ne jungiamuoju kanalu
|  | 61 | Käsikäyttö (ei tarp.muk. IV) | Manual control (no DCV) | Manuell styrning (ej behovsstyrd ventilation) | Handsteuerung (keine Bedarfssteuerung) | Obsługa ręczna (niewymagana) IV) | Käsikasutus (mittevajaduspõhine ventilatsioon) | Manuāla vadība (ne pēc vajadzības IV) | Rankinis valdymas (ne pagal poreikį IV)
|  | 62 | Kello-ohjaus (ei tarp.muk. IV) | Clock control (no DCV) | Klockstyrning (ej behovsstyrd ventilation) | Zeitsteuerung (keine Bedarfssteuerung) | Sterowanie zegarem (niewymagane) IV) | Kelljuhtimine (mittevajaduspõhine ventilatsioon) | Pulksteņvadība (ne pēc vajadzības IV) | Laikrodinis valdymas (ne pagal poreikį IV)
|  | 63 | Keskitetty tarp.muk. ohjaus | Central demand control | Central behovsstyrning | Zentrale Bedarfssteuerung | Scentralizowana kontrola w zależności od potrzeb | Tsentraalne vajaduspõhine juhtimine | Centralizēta vadība pēc vajadzības | Centralizuotas valdymas pagal poreikį
|  | 64 | Paikallinen tarp.muk. ohjaus | Local demand control | Lokal behovsstyrning | Steuerung nach örtlichem Bedarf | Lokalna kontrola w zależności od potrzeb | Kohalik vajaduspõhine juhtimine | Vietēja vadība pēc vajadzības | Vietinis valdymas pagal poreikį
|  | 65 | On/off & yksinopeuksinen | On/off & single speed | On/Off & enkelhastighets | Ein/aus und eine Drehzahl | Włączanie/wyłączanie i pojedyncza prędkość | Sisse/välja ja ühekiiruseline | Ieslēgts/izslēgts un vienātruma | Įjungta/išjungta ir vienas greitis
|  | 66 | Kaksinopeuksinen | 2-speed | 2-hastighets | 2 Drehzahlen | Dwubiegowy | Kahekiiruseline | Divātrumu | Du greičiai
|  | 67 | Moninopeuksinen | Multi-speed | Flerhastighets | mehrere Drehzahlen | Wieloprędkościowy | Mitmekiiruseline | Vairākātrumu | Daugiau greičių
|  | 68 | Portaaton säätö | Variable-speed | Steglös reglering | regelbare Drehzahl | Bezstopniowa regulacja | Sujuv reguleerimine | Bezpakāpju regulēšana | Tolygus reguliavimas
|  | 69 | Kylmä | Cold | Kall | Kalt | Zimny | Külm | Auksts | Šalta
|  | 70 | Keskiarvo | Average | Medelvärde | Durchschnitt | Umiarkowany | Keskmine | Vidējs | Vidutinė vertė
|  | 71 | Lämmin | Warm | Varm | Warm | Ciepły | Soe | Silts | Šilta
|  | 72 | Ilmanvaihdon poistoilman lämmöntalteenoton vuosihyötysuhteen laskenta | Calculation of annual efficiency for exhaust air heat recovery | Beräkning av årsverkningsgrad för värmeåtervinning av ventilationens frånluft | Berechnung des Jahresnutzungsgrades der Wärmerückgewinnung der Lüftungsabluft | Obliczanie rocznej sprawności odzysku ciepła z powietrza wywiewanego z wentylacji | Ventilatsiooni väljatõmbeõhu soojusvahetuse aastase kasuteguri arvutamine | Ventilācijas izplūstošā gaisa rekuperācijas ikgadējā lietderības koeficienta aprēķināšana | Metinio šilumos atgavimo iš ištraukiamo oro efektyvumo apskaičiavimas
|  | 73 | Laskenta YM:n Monisteen 122 mukaisesti | Calculations according to Handout 122 of the Finnish Ministry of the Environment | Beräkning enligt Finska Miljöministeriets kompendium 122 | Berechnungen gemäß Handout 122 des finnischen Umweltministeriums | Obliczenia zgodnie z Publikacją Ministerstwa Środowiska YM 122 | Arvutamine YM-i trükise 122 kohaselt | Aprēķins saskaņā ar Vides ministrijas kopiju Nr. 122 | Skaičiavimas pagal Aplinkos ministerijos leidinį Nr. 122
|  | 74 | = syötettävä solu | = insert value | = Infoga värde | = Wert eingeben | = wprowadzana komórka | = sisestatav lahter | = ievadāmais lauciņš | = įvesties langelis
|  | 75 | Laskennan lähtöarvot: | Calculation parameters: | Beräkningsparametrar: | Berechnungsparameter: | Wartości wyjściowe dla obliczeń: | Arvutuse lähteväärtused: | Aprēķinu izejas vērtības: | Skaičiavimo pradinės vertės:
|  | 76 | Tuloilmavirta, LTO:n läpi virtaava | Supply air volume flow, through heat recovery | Tilluftsflöde, genom värmeåtervinningssystem | Zuluft, die durch die Wärmerückgewinnung strömt | Przepływ powietrza nawiewanego przez wymiennik odzysku ciepła | Sissepuhkeõhu vooluhulk, läbi soojusvaheti | Ieplūstošā gaisa plūsma, caur rekuperatoru plūstošā | Tiekiamo oro srautas, tekantis per LTO
|  | 77 | Poistoilmavirta, LTO:n läpi virtaava | Extract air volume flow, through heat recovery | Frånluftsflöde, genom värmeåtervinningssystem | Abluft, die durch die Wärmerückgewinnung strömt | Przepływ powietrza wywiewanego przez wymiennik odzysku ciepła | Väljatõmbeõhu vooluhulk, läbi soojusvaheti | Izplūstošā gaisa plūsma, caur rekuperatoru plūstošā | Ištraukiamo oro srautas, tekantis per LTO
|  | 78 | LTO:n läpi virtaavan tulo- ja poistoilmavirran suhde | Supply air to extract air ratio for volume flow through heat recovery | Förhållande av till- och frånluftsflöde genom värmeåtervinningen. | Das Verhältnis von Zuluft und Abluft Ströme durch die Wärmerückgewinnung | Stosunek przepływu powietrza nawiewanego i wywiewanego przez wymiennik odzysku ciepła | Läbi soojusvaheti voolava sissepuhkeõhu ja väljapuhkeõhu vooluhulga suhe | Caur rekuperatoru plūstošās ieplūstošās un izplūstošās gaisa plūsmas attiecība | Tiekiamo ir ištraukiamo oro srauto per LTO santykis
|  | 79 | LTO-vaatimuksen piiriin kuuluva erillispoistoilmavirta | Additional extract air flow rate included in heat recovery requirements | Ytterligare frånluft ingår i värmeåtervinningskraven | Zusatsabluft in den Wärmerückgewinnungsanforderungen enthalten | Dodatkowy przepływ powietrza wywiewanego trafiający na wymiennik odzysku ciepła | Soojusvaheti nõude alla kuuluv väljatõmbeõhu eriõhuvool | Rekuperatora darbības prasībās ietvertā atsevišķā izplūstošā gaisa plūsma | Atskiras ištraukiamo oro srautas, kuriam taikomas LTO reikalavimas
|  | 80 | Em. erillispoistoilman käyttöaika | Operational time of the additional extract air | Drifttid för ovan nämnda extra frånluft | Betriebsdauer der obenkenannten zusätzlichen Abluft | Czas korzystania z powyższego oddzielnego wyciągu powietrza | Näiteks eriväljatõmbeõhu kasutusaeg | Iepriekš minētās atsevišķās izplūstošās gaisa plūsmas izmantošanas laiks | Minėto atskiro ištraukiamo oro naudojimo laikas
|  | 81 | Koko IV:n tulo- ja poistoilmavirtojen suhde | Supply / extract air volume flow ratio for entire ventilation system | Förhållande av till- och frånluftsflöde genom värmeåtervinningen. | Das Verhältnis von Zuluft und Abluft für das gesamte Lüftungssystem | Stosunek przepływów powietrza nawiewanego i wywiewanego dla całego systemu wentylacyjnego | Kogu ventilatsiooni sissepuhke ja väljatõmbe õhuvoolude suhe | Visu IV ieplūstošo un izplūstošo gaisa plūsmu attiecība | Tiekiamo ir ištraukiamo oro srautų santykis visame IV
|  | 82 | Tuloilman lämpötilahyötysuhde yhtä suurilla ilmavirroilla (EN 13141-7) | Supply side temperature ratio for balanced air flow (EN 13141-7) | Temperaturverkningsgrad för tilluft vid motsvarande luftflöde (EN 13141-7) | Zulufts Temperatureffizienz bei gleichen Luftströmen (EN 13141-7) | Wydajność temperaturowa powietrza nawiewanego przy równych przepływach powietrza (EN 13141-7) | Sissepuhkeõhu temperatuuri kasutegur samade õhuvoolude korral (EN 13141-7) | Ieplūstošā gaisa temperatūras pārneses lietderības koeficients vienlīdz lielām gaisa plūsmām (EN 13141-7) | Tiekiamo oro temperatūros efektyvumo koeficientas esant vienodiems oro srautams (EN 13141-7)
|  | 83 | Tuloilman lämpötilahyötysuhde | Supply side temperature ratio | Temperaturverkningsgrad för tilluft | Zulufts Temperatureffizienz | Wydajność temperaturowa powietrza nawiewanego | Sissepuhkeõhu temperatuuri kasutegur | Ieplūstošā gaisa temperatūras pārneses lietderības koeficients | Tiekiamo oro temperatūros efektyvumo koeficientas
|  | 84 | Säävyöhyke | Climate zone | Klimatzon | Klimazone | Strefa klimatyczna | Kliimavöönd | Meteoroloģiskā zona | Klimato juosta
|  | 85 | Sisälämpötila | Indoor temperature | Inomhustemperatur | Innenlufttemperatur | Temperatura wewnętrzna | Sisetemperatuur | Iekštelpu temperatūra | Vidaus temperatūra
|  | 86 | Minimi jäteilman lämpötila | Minimum exhaust air temperature | Minimitemperatur för avluft | Minimale Fortlufttemperatur | Minimalna temperatura powietrza wyrzucanego | Minimaalne heitõhu temperatuur | Piesārņotā gaisa minimālā temperatūra | Minimali išeinančio oro temperatūra
|  | 87 | Maksimi tuloilman lämpötila rajoitetussa tilanteessa | Maximum supply air temperature in a limited situation | Maximitemperatur för tilluft i ett begränsad läge | Maximale Zulufttemperatur in einer begrenzten Situation | Maksymalna temperatura powietrza nawiewanego w ograniczonej sytuacji | Maksimaalne sissepuhkeõhu temperatuur piiratud olukorras | Maksimālā ieplūstošā gaisa temperatūra ierobežotā situācijā | Didžiausia tiekiamo oro temperatūra ribotoje padėtyje
|  | 88 | Vuosihyötysuhde | Annual efficiency | Årsverkningsgrad | Jährliche Effizienz | Roczny współczynnik efektywności energetycznej | Aastane kasutegur | Gada lietderības koeficients | Metinis efektyvumo koeficientas
|  | 89 | Ilmanvaihdon kokonaisenergiantarve | Total energy demand for ventilation | Totalt energibehov för ventilation | Gesamtenergiebedarf für Lüftung | Całkowite zapotrzebowanie na energię dla wentylacji | Ventilatsiooni koguenergiavajadus | Kopējais ventilācijai nepieciešamās enerģijas daudzums | Bendras vėdinimo sistemos energijos poreikis
|  | 90 | Talteenotettu lämmitysenergia | Recovered heating energy | Återvunnen värmeenergi | Zurückgewonnene Heizenergie | Odzyskana energia grzewcza | Salvestatud kütteenergia | Rekuperētā siltumenerģija | Atgauta šilumos energija
|  | 91 | Tuloilman lämpötila LTO:n jälkeen | Supply air temperature after heat exchanger | Tilluftstemperatur efter värmeåtervinning | Zulufttemperatur nach Wärmerückgewinnung | Temperatura powietrza nawiewanego po LTO | Sissepuhkeõhu temperatuur pärast soojusvahetit | Ieplūstošā gaisa temperatūra pēc rekuperatora | Tiekiamo oro temperatūra po LTO
|  | 92 | Tuloilman lämpötila [°C] | Supply air temperature [°C] | Tilluftstemperatur [°C] | Zulufttemperatur [°C] | Temperatura powietrza nawiewanego [°C] | Sissepuhkeõhu temperatuur [°C] | Ieplūstošā gaisa temperatūra [°C] | Tiekiamo oro temperatūra [°C]
|  | 93 | Ulkoilman lämpötila [°C] | Outdoor air temperature [°C] | Uteluftstemperatur [°C] | Außenlufttemperatur [°C] | Temperatura powietrza zewnętrznego [°C] | Välisõhu temperatuur [°C] | Āra gaisa temperatūra [°C] | Lauko oro temperatūra [°C]
|  | 94 | Jäteilman lämpötila | Exhaust air temperature | Avluftstemperatur | Fortlufttemperatur | Temperatura zużytego powietrza | Heitõhu temperatuur | Piesārņotā gaisa temperatūra | Išeinančio oro temperatūra
|  | 95 | Jäteilman lämpötila [°C] | Exhaust air temperature [°C] | Avluftstemperatur [°C] | Fortlufttemperatur [°C] | Temperatura zużytego powietrza [°C] | Heitõhu temperatuur [°C] | Piesārņotā gaisa temperatūra [°C] | Išeinančio oro temperatūra [°C]
|  | 96 | Ulkoilman lämpötila [°C] | Outdoor air temperature [°C] | Uteluftstemperatur [°C] | Außenlufttemperatur [°C] | Temperatura powietrza zewnętrznego [°C] | Välisõhu temperatuur [°C] | Āra gaisa temperatūra [°C] | Lauko oro temperatūra [°C]
|  | 97 | Aika vuodessa | Percentage of the year | Tid av året i procent | Anteil des Jahres | Czas w roku | Aeg aastas | Laiks gadā | Metų laikas
|  | 98 | Jäteilman lämpötila | Exhaust air temperature | Avlufts-temperatur | Fortluft-temperatur | Temperatura zużytego powietrza | Heitõhu temperatuur | Piesārņotā gaisa temperatūra | Išeinančio oro temperatūra
|  | 99 | Tuloilman lämpötila | Supply air temperature | Tillufts-temperatur | Zuluft-temperatur | Temperatura powietrza nawiewanego | Sissepuhkeõhu temperatuur | Ieplūstošā gaisa temperatūra | Tiekiamo oro temperatūra
|  | 100 | Yhteensä | Total | Summa | Gesamt | Razem | Kokku | Kopā | Iš viso
|  | 101 | SS,Kd = sisä- ja ulkoilman lämpötilan välinen lämmöntarveluku, Kd | SI,Kd = heating degree days, between indoor air and outdoor air, Kd | SI,Kd = graddagstal, mellan inne- och uteluft, Kd | SI,Kd = Wärmesumme, Innenluft - Außenluft, Kd | SS,Kd = współczynnik rozszerzalności cieplnej między temperaturą powietrza wewnętrznego i zewnętrznego, Kd | SS,Kd = sise- ja välisõhu temperatuuri vaheline soojusvajadusarv, Kd | SS,Kd = iekštelpu un āra gaisa temperatūras savstarpējais nepieciešamā siltuma koeficients, Kd | SS, Kd = šilumos poreikio tarp patalpos ir lauko oro temperatūros koeficientas, Kd
|  | 102 | ST,Kd = tulo- ja ulkoilman lämpötilan välinen lämmöntarveluku, Kd | SS,Kd = heating degree days, between supply air and outdoor air, Kd | SS,Kd = graddagstal, mellan till- och uteluft, Kd | SZ,Kd = Wärmesumme, Zuluft - Außenluft, Kd | ST,Kd = współczynnik rozszerzalności cieplnej między temperaturą powietrza nawiewanego i zewnętrznego, Kd | SS,Kd = sissepuhkeõhu ja välisõhu temperatuuri vaheline soojusvajadusarv, Kd | ST,Kd = ieplūstošā un āra gaisa temperatūras savstarpējais nepieciešamā siltuma koeficients, Kd | ST, Kd = šilumos poreikio tarp tiekiamo ir lauko oro temperatūros koeficientas, Kd
|  | 103 | SJ,Kd = jäte- ja ulkoilman lämpötilan välinen lämmöntarveluku, Kd | SE,Kd = heating degree days, between exhaust air and outdoor air, Kd | SE,Kd = graddagstal, mellan från- och uteluft, Kd | SF,Kd = Wärmesumme, Fortluft - Außenluft, Kd | SJ,Kd = współczynnik przenikania ciepła między powietrzem a temperaturą powietrza zewnętrznego, Kd | SJ,Kd = heitõhu ja välisõhu temperatuuri vaheline soojusvajadusarv, Kd | SJ,Kd = piesārņotā un āra gaisa temperatūras savstarpējais nepieciešamā siltuma koeficients, Kd | SJ, Kd = šilumos poreikio tarp išeinančio ir lauko oro temperatūros koeficientas, Kd
|  | 104 | Vesikiertoisen lämmityspatterin mitoitus | Dimensioning of water-based heating coil | Dimensionering av vattenburet värmebatteri | Dimensionierung von Heizregistern | Dobór nagrzewnicy wodnej | Vesiringlusega kalorifeeri arvutus | Ūdens cirkulācijas apsildes radiatora dimensionēšana | Radiatoriaus su vandens cirkuliacija matmenys
|  | 105 | Ei käytettävissä tässä mallissa | Not available for selected model | Ej tillgänglig för denna modell | Für das ausgewählte Modell nicht verfügbar | Niedostępne w tym modelu | Ei ole selle mudeli puhul kasutatav | Šim modelim nav izmantojams | Šiame modelyje nėra
|  | 106 | Syötä mitoitus- ja tavoitearvot: | Insert parameters: | Fyll i dimensionerings- och målvärden: | Parameter einfügen: | Wprowadź rozmiar i wartości docelowe: | Sisesta arvutus- ja sihtväärtused: | Ievadīt dimensionēšanas un mērķa vērtības: | Įveskite matmenis ir tikslines vertes:
|  | 107 | Aloita syöttämällä joko meno- tai paluuveden lämpötila | Start by inserting either inlet or outlet water temperature | Börja med att fylla i temperatur för tillopps- eller returvatten | Beginnen Sie mit der Eingabe entweder der Einlass- oder der Auslasswassertemperatur | Rozpocznij od wprowadzenia temperatury wody zasilającej lub powrotnej | Alustuseks sisesta kas välja- või tagasivooluvee temperatuur | Sākt ievadi, ievadot turpgaitas vai atpakaļgaitas ūdens temperatūru | Pirmiausia įveskite įleidžiamo arba grįžtančio vandens temperatūrą
|  | 108 | Patterille tulevan ilman lämpötila | Inlet air temperature | Lufttemperatur vid batteriingång | Einlasslufttemperatur | Temperatura powietrza na wejściu | Kalorifeeri siseneva õhu temperatuur | Pie radiatora pieplūstošā gaisa temperatūra | Į radiatorių įeinančio oro temperatūra
|  | 109 | Patterilta lähtevän ilman lämpötila | Outlet air temperature | Lufttemperatur vid batteriutgång | Auslasslufttemperatur | Temperatura powietrza na wyjściu | Kalorifeerist väljuva õhu temperatuur | No radiatora aizplūstošā gaisa temperatūra | Iš radiatoriaus išeinančio oro temperatūra
|  | 110 | Menoveden lämpötila | Inlet water temperature | Temperatur för tilloppsvatten | Wassereinlasstemperatur | Temperatura wody zasilającej | Väljuva vee temperatuur | Turpgaitas ūdens temperatūra | Įleidžiamo vandens temperatūra
|  | 111 | Paluuveden lämpötila | Outlet water temperature | Temperatur för returvatten | Wasserauslasstemperatur | Temperatura wody powrotnej | Tagasivooluvee temperatuur | Atpakaļgaitas ūdens temperatūra | Grįžtančio vandens temperatūra
|  | 112 | Tuloilman tilavuusvirta | Supply air volume flow | Tilluftens volymflöde | Zuluftvolumenstrom | Przepływ objętościowy powietrza nawiewanego | Sissepuhkeõhu vooluhulk | Ieplūstošā gaisa tilpuma plūsma | Tiekiamo oro srautas
|  | 113 | Tarvittava lämmitysteho: | Required heating power | Värmeeffektbehov | Erforderliche Heizleistung | Wymagana moc grzewcza: | Vajalik küttevõimsus: | Nepieciešamā apsildes jauda: | Reikalinga šildymo galia:
|  | 114 | * Käytettäessä Oras DN15S suurtehorunkoa + Stabila -patteriventtiiliä (täysin auki, KV = 1,00) | *Using Oras DN15S Radiator valve body & Stabila radiator valve (fully open, CV = 1.00) | * Vid användning av Oras DN15S radiatorventilshus + Stabila radiatorventil (fullt öppen, CV = 1,00) | Bei Verwendung von Oras DN15S + Stabila -Heizkörperventil (vollständig geöffnet, CV = 1.00) | * W przypadku korzystania z korpusu o dużej pojemności Oras DN15S + zaworu grzejnikowego Stabila (całkowicie otwarty, KV = 1,00) | * Kasutades Oras DN15S suurt korpust + Stabila kalorifeeri ventiili (täielikult avatud, KV = 1,00) | * Izmantojot Oras DN15S lieljaudas korpusu + Stabila radiatora ventili (pilnīgi atvērtu, KV = 1,00) | * Naudojant didelės galios „Oras DN15S“ korpusą + „Stabila“ radiatoriaus vožtuvą (visiškai atidarytas, KV = 1,00)
|  | 115 | Patterimitoitus menoveden lämpötilan mukaan | Heating coil dimensioning by inlet water temperature | Batteridimensionering baserat på temperatur för tilloppsvatten | Dimensionierung entsprechend der Einlasswassertemperatur | Dobór nagrzewnicy w zależności od temperatury wody zasilającej | Kalorifeeri arvutus vastavalt väljuva vee temperatuurile | Radiatoru dimensionēšana atbilstoši turpgaitas ūdens temperatūrai | Radiatoriaus matmenys pagal įleidžiamo vandens temperatūrą
|  | 116 | Patterimitoitus paluuveden lämpötilan mukaan | Heating coil dimensioning by outlet water temperature | Batteridimensionering baserat på temperatur för returvatten | Dimensionierung entsprechend der Auslasswassertemperatur | Dobór nagrzewnicy w zależności od temperatury wody powrotnej | Kalorifeeri arvutus vastavalt tagasivooluvee temperatuurile | Radiatoru dimensionēšana atbilstoši atpakaļgaitas ūdens temperatūrai | Radiatoriaus matmenys pagal grįžtančio vandens temperatūrą
|  | 117 | Menoveden lämpötila | Inlet water temperature | Temperatur för tilloppsvatten | Einlasswassertemperatur | Temperatura wody zasilającej | Väljuva vee temperatuur | Turpgaitas ūdens temperatūra | Įleidžiamo vandens temperatūra
|  | 118 | Paluuveden lämpötila | Outlet water temperature | Temperatur för returvatten | Auslasswassertemperatur | Temperatura wody powrotnej | Tagasivooluvee temperatuur | Atpakaļgaitas ūdens temperatūra | Grįžtančio vandens temperatūra
|  | 119 | Virtaama | Volume flow | Volymflöde | Volumenstrom | Natężenie przepływu | Vooluhulk | Plūsma | Srautas
|  | 120 | Patterin nestepuolen painehäviö | Heating coil fluid side pressure loss | Tryckfall för vätskesidan av värmebatteri | Flüssigkeitsseitiger Druckabfall der Heizregister | Spadek ciśnienia po stronie cieczy w nagrzewnicy | Kalorifeeri vedelikupoole rõhukadu | Radiatora šķidruma spiediena zudums | Radiatoriaus skysčio slėgio sumažėjimas
|  | 121 | Säätöventtiilin painehäviö (Airfi toteutus)* | Control valve pressure loss (Airfi implementation)* | Tryckfall för reglerventil* | Druckverlust des Regelventils* | Spadek ciśnienia na zaworze sterującym* | Reguleerventiili rõhukadu* | Regulācijas ventiļa spiediena zudums* | Slėgio sumažėjimas valdymo vožtuve*
|  | 122 | Virtausnopeus patterin putkireitissä | Flow rate in the coil's pipe circuit | Flödeshastighet | Fliessgeschwindigkeit | Prędkość przepływu | Voolukiirus | Plūsmas ātrums | Srauto greitis
|  | 123 | Pistotulppa 230 V, 50 Hz, 10 A, max 1100 W | Electric plug 230 V, 50 Hz, 10 A, max 1100 W | Stickkontakt 230 V, 50 Hz, 10 A, max 1100 W | Stecker 230 V, 50 Hz, 10 A, max 1100 W | Wtyczka 230 V, 50 Hz, 10 A, maks. 1100 W | Pistik 230 V, 50 Hz, 10 A, max 1100 W | Kontaktspraudnis 230 V, 50 Hz, 10 A, maks. 1100 W | Kištukas 230 V, 50 Hz, 10 A, maks. 1100 W
|  | 124 | Sähkönsyöttö: | Power supply: | Strömförsörjning: | Stromversorgung: | Zasilanie elektryczne: | Elektritoide: | Elektrības padeve: | Elektros tiekimas:
|  | 125 | käytettäessä 'dB-pakettia' (Huom! Vaatii kaappirungon) | using 'dB-paketti' (NB! Requires a cabinet) | Vid använding av 'dB-paketti' (Obs! Kräver en skåpram) | mit Schallgedämmtes Gehäuse "dB-paketti" (N.B. Braucht einen Schrankrahmen) | podczas korzystania z "pakietu dB" (Uwaga! Wymaga ramy szafki) | kasutades 'dB-paketti' (NB! Nõuab kapiraami) | izmantojot 'dB-paketi' (Uzmanību! Nepieciešams skapja korpuss) | naudojant „dB paketą“ (Dėmesio! Reikalingas rėminis korpusas)
|  | 126 | Valitse laitemallin yhteydessä vesikiertoinen lämmityspatteri | Select heating coil in the model selection menu | Välj värmebatteri vid val av modell | Wasser-Heizregister im Modellauswahlmenü auswählen | Wybierz chłodnicę chłodzoną wodą dla swojego modelu | Vali seadmemudeli puhul vesiringlusega kalorifeer | Kopā ar iekārtas modeli izvēlieties ūdens cirkulācijas radiatoru | Rinkdamiesi įrangos modelį, pasirinkite šildymo radiatorių su vandens cirkuliacija
|  | 127 | Ei käyttöalueella. Tarkista mitoitusarvot. | Value out of range. Check input parameters. | Ej på användningsområdet. Kontrollera dimensioneringsvärden. | Wert außerhalb des Verwendungsbereichs. Parameter prüfen. | Nie w obszarze użytkowania. Sprawdź wartości wymiarowe | Pole kasutusalas. Kontrolli arvutusväärtusi. | Nav ekspluatācijas diapazonā. Pārbaudīt dimensionēšanas vērtības. | Naudojimo zonoje nėra. Patikrinkite matmenų vertes.
|  | 128 | Äänenvaimennuskotelo ei käytettävissä tässä mallissa | Sound insulated casing not available for selected model | Ljudisolerat hölje ej tillgängligt för denna modell. | Schallgedämmtes Gehäuse für ausgewähltes Modell nicht verfügbar | Obudowa z redukcją szumów nie jest dostępna dla tego modelu | Mürasummutuskate ei ole selle mudeli puhul kasutatav | Skaņu slāpējošs korpuss šim modelim nav pieejams | Garso slopinimo gaubto šiame modelyje nėra
|  | 129 | * Huom. keittiöohitusta käytettäessä kokonaispoistoilmavirta syötettyä mitoitusarvoa suurempi | * With kitchen bypass, the total extract air volume flow is larger than the inserted value | * Vid användning av förbigång för kök är totala frånluftsvolymflödet större än det insatta dimensioneringsvärdet. | * Bei Küchen-bypass ist der Gesamtabluftvolumenstrom größer als der eingegebene Wert | * Uwaga: W przypadku korzystania z okapu kuchennego całkowity przepływ powietrza wylotowego jest wyższy niż wartość znamionowa wejścia. | * NB! Köögi möödavoolu kasutamisel on väljatõmbeõhu õhuvoolu väärtus sisestatud arvutusväärtusest suurem | * Uzmanību: ja tiek apieta virtuve, kopējā izplūstošā gaisa plūsma ir lielāka par ievadīto dimensionēšanas vērtību | * Pastaba: naudojant virtuvės apylanką, bendras ištraukiamo oro srautas yra didesnis už įvestą išmatuotą vertę.
|  | 130 | Säävyöhyke (valtio/maa) | Climate zone (state/country) | Klimatzon (stat/land) | Klimazone (Staat/Land) | Strefa klimatyczna (kraj) | Kliimavöönd (riik/maa) | Meteoroloģiskā zona (valsts/teritorija) | Klimato juosta (valstybė / šalis)
|  | 131 | Säävyöhyke (kunta/kaupunki) | Climate zone (municipality/city) | Klimatzon (kommun/stad) | Klimazone (Gemeinde/Stadt) | Strefa klimatyczna (gmina/miasto) | Kliimavöönd (vald/linn) | Meteoroloģiskā zona (pašvaldība/pilsēta) | Klimato juosta (savivaldybė / miestas)
|  | 132 | Ilman tilavuusvirta [m³/h] | Air volume flow [m³/h] | Luftens volymflöde [m³/h] | Luftvolumenstrom [m³/h] | Natężenie przepływu powietrza [m³/h] | Õhu vooluhulk [m³/h] | Gaisa tilpuma plūsma [m³/h] | Oro srautas [m³/h]
|  | 133 | Mitoituspiste (syötä tilavuusvirta ja paine-ero) | Operating point (insert air flow and pressure difference values): | Driftpunkt (ange luftflöde och tryckdifferensvärden): | Betriebspunkt (Geben Sie Luftvolumenstrom- und Druckdifferenzwerte ein): | Punkt wymiarowania (wprowadź przepływ objętościowy i różnicę ciśnień) | Arvutuspunkt (sisesta vooluhulk ja rõhuerinevus) | Dimensionēšanas punkts (ievadīt tilpuma plūsmu un spiediena starpību) | Matavimo taškas (įveskite srautą ir slėgio skirtumą)
|  | 134 | Tehostustilanteen laskenta: | Boost situation calculation: | Beräkning av forceringssituation: | Berechnung der Verstärkungssituation: | Obliczenie zapasu wydajności jednostki: | Võimendusolukorra arvutamine: | Efektivitātes palielināšanas situācijas aprēķins: | Galingumo didinimo apskaičiavimas:
|  | 135 | Maksimi tehostusvara: | Maximum boost reserve: | Maximal forceringsreserv: | Maximale Verstärkungsreserve: | Maksymalny zapas wydajności: | Maksimaalne võimendusvaru: | Maksimālā efektivitātes palielināšana: | Didžiausias galingumo padidinimas:
|  | 136 | Syötä haluttu tehostusarvo: | Insert the desired boost value: | Ange forceringsvärde: | Verstärkungswert eingeben: | Wprowadź żądaną wartość zapasu wydajności: | Sisesta soovitud võimendusväärtus: | Ievadīt vēlamo efektivitātes palielināšanas vērtību: | Įveskite norimą galingumo padidinimo vertę:
|  | 137 | Tehostusarvo [%]: | Boost value [%]: | Forceringsvärde [%]: | Verstärkungswert [%]: | Wartość zapasu wydajności [%]: | Võimendusväärtus [%]: | Efektivitātes palielināšanas vērtība [%]: | Galingumo padidinimo vertė [%]:
|  | 138 | Toimintapiste tehostustilanteessa: | Operating point in boost situation: | Driftpunkt i forceringssituation: | Betriebspunkt in der Verstärkungssituation: | Punkt pracy w przypadku użycia programu TURBO: | Toimimiskoht võimendusolukorras: | Darbības punkts efektivitātes palielināšanas situācijā: | Veikimo taškas galingumo padidinimo atveju:
|  | 139 | Määritettyä tehostusarvoa ei saavutettu | The specified boost value was not achieved | Det angivna forceringsvärdet uppnåddes inte | Der festgelegte Verstärkungswert wurde nicht erreicht | Zdefiniowana wartość wydajności nie została osiągnięta | Määratud võimendusväärtust ei saavutatud | Noteiktā efektivitātes palielināšanas vērtība nav sasniegta | Nustatyta galingumo padidinimo vertė nebuvo pasiekta
|  | 140 | Laskenta YM:n Monisteen 122 mukaisesti |  |  |  | Obliczenia zgodnie z Publikacją Ministerstwa Środowiska YM 122 | Arvutamine YM-i trükise 122 kohaselt | Aprēķins saskaņā ar Vides ministrijas kopiju Nr. 122 | Skaičiavimas pagal Aplinkos ministerijos leidinį Nr. 122
|  | 141 | Sovelletut asiakirjat ja standardit: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Tasauslaskentaopas 2018, YM moniste 122 ja Komission asetukset (EU) N:o 1253/2014 & N:o 1254/2014. Emme vastaa ohjelman mahdollisista virheistä tai niiden aiheuttamista välittömistä tai välillisistä virheistä. | Applied documents and standards: SFS-EN 13141-7, LVI 30-10529, Finnish Ministry of the Environment: Decree 1009/2017, and Commission Regulations (EU) No 1253/2014 & No 1254/2014. We do not answer for the direct or indirect harm caused by possible errors in the selection program. | Tillämpade dokument och standarder: SFS-EN 13141-7, LVI 30-10529, Finska Miljöministeriets förordning 1009/2017, samt kommisionens förordningar (EU) nr 1253//2014 & nr 1254/2014. Vi ansvarar inte för direkt eller indirekt skada orsakad av möjliga fel i produktvalprogrammet. | Angewandte Dokumente und Normen: SFS-EN 13141-7, LVI 30-10529, Finnisches Umweltministerium: Dekret 1009/2017 und Verordnung (EU) Nr. 1253/2014 & 1254/2014 Der Kommission. Wir sind nicht verantwortlich für direkte oder indirekte Schäden, die durch mögliche Fehler im Auswahlprogramm verursacht werden. | Obowiązujące dokumenty i normy: SFS-EN 13141-7, LVI 30-10529, Rozporządzenie Ministerstwa Środowiska YMa1009/2017, Przewodnik bilansowania 2018, Publikacja Ministerstwa Środowiska YM 122 oraz rozporządzenia Komisji (UE) nr 1253/2014 i nr 1254/2014. Nie ponosimy odpowiedzialności za jakiekolwiek błędy w programie ani za jakiekolwiek bezpośrednie lub pośrednie błędy przez nie spowodowane. | Kohaldatud dokumendid ja standardid: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, Ühtlustamisarvutuste juhend 2018, YM paljundus 122 ja Komisjoni määrused (EL) nr 1253/2014 ja nr 1254/2014. Me ei vastuta tarkvara võimalike puuduste ega nendest tulenevate otseste või kaudsete vigade eest. | Izmantotie dokumenti un standarti: SFS-EN 13141-7, LVI 30-10529, Vides ministrijas dekrēts 1009/2017, Balansēšanas aprēķina rokasgrāmata 2018, Vides ministrijas kopija Nr. 122 un Komisijas Regulas (ES) Nr. 1253/2014 un Nr. 1254/2014. Nenesam atbildību par iespējamām kļūdām programmā vai to izraisītām tiešām vai netiešām kļūdām. | Taikyti dokumentai ir standartai: SFS-EN 13141-7, LVI 30-10529, YMa 1009/2017, 2018 m. skaičiavimo vadovas, Aplinkos ministerijos leidinys 122 ir Komisijos reglamentai (ES) Nr. 1253/2014 ir Nr. 1254/2014. Neatsakome už jokias programos klaidas ar dėl jų atsiradusias tiesiogines ar netiesiogines paklaidas.
|  | 142 | Valitse säävyöhyke (kaupunki) | Select climate zone (city) | Välj klimatzon (kommun/stad) | Wählen Sie die klimazone (Stadt) | Wybierz strefę klimatyczną (miasto) | Kliimavööndi valimine (linn) | Izvēlēties meteoroloģisko zonu (pilsēta) | Pasirinkite klimato juostą (miestas)
|  | 143 | Huom. yllä olevat arvot sisältävät myös laitteen elektroniikan. | Note: The above values also include the device's electronics. | De ovanstående värdena inkluderar också enhetens elektronik. | Die obigen Werte beinhalten auch die Elektronik des Geräts. | Uwaga: Powyższe wartości obejmują również zużycie energii przez elektronikę urządzenia. | NB! Ülaltoodud väärtused hõlmavad ka seadme elektroonikat. | Uzmanību: iepriekš minētās vērtības ietver arī iekārtas elektroniku. | Pastaba: į pirmiau nurodytas vertes įskaičiuota ir prietaiso elektronika.
|  | 144 | Lämmöntalteenottokennon hyötysuhde (EN 308) | Heat recovery cell efficiency (EN 308) | Verkningsgrad för värmeåtervinningscell (EN 308) | Wirkungsgrad der Wärmerückgewinnungszelle (EN 308) | Sprawność wymiennika odzysku ciepła (EN 308) | Soojusvaheti kasutegur (EN 308) | Rekuperatora elementa lietderības koeficients (EN 308) | Šilumos atgavimo elemento efektyvumo koeficientas (EN 308)
|  | 145 | Puhaltimien ja elektroniikan sähkönkulutus | Electricity consumption of fans and electronics | Elkonsumtion för fläktar och elektronik | Stromverbrauch von Ventilatoren und Elektronik | Zużycie energii elektrycznej przez wentylatory i elektronikę | Ventilaatorite ja elektroonika voolutarve | Ventilatora un elektronikas strāvas patēriņš | Ventiliatorių ir elektronikos įtaisų elektros sąnaudos
|  | 146 | Tuloilman lämpötilan rajoitus | Supply air temperature limitation | Begränsning av tilluftstemperatur | Begrenzung der Zulufttemperatur | Ograniczenie temperatury powietrza nawiewanego | Sissepuhkeõhu temperatuuri piirang | Ieplūstošā gaisa temperatūras ierobežojums | Tiekiamo oro temperatūros apribojimas
|  | 147 | Rajoitettu | Limited | Begränsad | Begrenzt | Ograniczone | Piiratud | Ierobežots | Apribota
|  | 148 | Ei rajoitusta | No limitation | Ingen begränsning | Keine Begrenzung | Brak ograniczenia | Piiranguteta | Neierobežots | Neribojama
|  | 149 | Tuloilman tavoitelämpötila | Target supply air temperature | Målinställd temperatur för tilluften | Ziel-Zulufttemperatur | Docelowa temperatura powietrza nawiewanego | Sissepuhkeõhu soovitud temperatuur | Ieplūstošā gaisa mērķa temperatūra | Pageidaujama tiekiamo oro temperatūra
|  | 150 | Mitoittava ulkoilman minimilämpötila | Design minimum outdoor air temperature | Dimensionerande utomhustemperatur | Auslegungsmindestaußentemperatur | Minimalna mierzalna temperatura powietrza zewnętrznego | Arvutatav minimaalne välisõhu temperatuur | Dimensionēšanas minimālā āra gaisa temperatūra | Mažiausia išmatuojama lauko oro temperatūra
|  | 151 | Tarvittava jälkilämmityspatterin ottoteho | Required reheating power | Utgångseffekt för eftervärmningsbatteriet | Abgabeleistung des Nachheizregisters | Wymagana moc wejściowa wymiennika dogrzewania wtórnego | Vajalik järelküttekalorifeeri võimsusvajadus | Nepieciešamā pēcapsildes radiatora ieejas jauda | Reikiama pašildymo radiatoriaus įsiurbimo galia
|  | 152 | Jälkilämmityspatterin maksimiteho | Maximum power of the reheater | Maximal effekt för eftervärmningsbatteriet | Maximalleistung des Nachheizregisters | Maksymalna moc wymiennika dogrzewania wtórnego | Järelsoojenduskalorifeeri maksimaalne võimsus | Pēcapsildes radiatora maksimālā jauda | Didžiausia pašildymo radiatoriaus galia
|  | 153 | Airfi: C-sarjan koneiden laitekoodin valinta | Airfi: Device code selection for C-series units
|  | 154 | Valitse vaihtoehto jokaisesta alla olevasta liukuvalikosta | Select an option from each dropdown menu below
|  | 155 | Koodiavain: | Code Key:
|  | 156 | Valinta: | Selection:
|  | 157 | PERUSRAKENNE: | BASIC STRUCTURE:
|  | 158 | SUODATUS: | FILTERS:
|  | 159 | PATTERIT: | COILS:
|  | 160 | TARVIKKEET: | ACCESSORIES:
|  | 161 | OHJAUKSET: | CONTROLS:
|  | 162 | Perusrakenne: | Basic structure:
|  | 163 | Suodatus: | Filters:
|  | 164 | Patterit: | Coils:
|  | 165 | Tarvikkeet: | Accessories:
|  | 166 | Ohjaukset: | Controls:
|  | 167 | (A ) Konetyyppi | (A) Unit type
|  | 168 | ( BBB ) Konekoko | (BBB) Unit size
|  | 169 | ( C ) Kätisyys - Huom! Varmista kanavajärjestys | (C) Unit orientation – Note! Ensure the ductwork configuration
|  | 170 | ( D ) Koneen automatiikka | (D) Unit automation
|  | 171 | ( E ) Suodatus TULO | (E) Supply air filtration
|  | 172 | ( F ) Suodatus POISTO | (F) Exhaust air filtration
|  | 173 | ( GG ) Jälkilämmityspatteri, sisäinen | (GG) Internal post-heating
|  | 174 | ( H ) Jälkilämmityksen ohjaus, sisäinen | (H) Internal post-heating control
|  | 175 | ( I ) Jäähdytyspatteri, sisäinen | (I) Internal cooling
|  | 176 | ( J ) Jäähdytyksen ohjaus, sisäinen jäähdytyspatteri | (J) Internal cooling control (cooling coil)
|  | 177 | ( K ) Suodatinvahti* | (K) Filter monitor*
|  | 178 | ( L ) Vakiopainesäätö* | (L) Constant pressure regulator*
|  | 179 | ( M ) Ilmamäärämittaus* | (M) Air volume flow measurement*
|  | 180 | ( N ) Jousipalautteiset sulkupellit | (N) Spring-return dampers
|  | 181 | ( O ) Mittausanturit, sisäinen * | (O) Internal measurement sensors*
|  | 182 | ( P ) Energiamittaus ** | (P) Energy meter**
|  | 183 | ( Q ) Ohjaus1- toimitus irrallaan, asennus työmaalla | (Q) Control 1 – delivered separately, installed on-site
|  | 184 | ( RR ) Ohjaus2- toimitus irrallaan, asennus työmaalla | (RR) Control 2 – delivered separately, installed on-site
|  | 185 | ( S ) Lisäinfo | (S) Additional information
|  | 186 | VALITTU MALLI JA KOODIAVAIN: | SELECTED MODEL AND CODE KEY:
|  | 187 | Koodi: | Code:
|  | 188 | Sisältökuvaus: | Content description:
|  | 189 | VESIKIERTOISTEN LÄMMITYS- JA JÄÄHDYTYSPATTERIEN MITOITUS | DIMENSIONING OF WATER-BASED HEATING AND COOLING COILS
|  | 190 | Vesikiertoisen jäähdytyspatterin mitoitus | Dimensioning of water-based cooling coil
|  | 191 | Patterille tulevan ilman suhteellinen kosteus | Inlet air relative humidity
|  | 192 | Tarvittava jäähdytysteho (tuntuva) | Required cooling capacity (sensible)
|  | 193 | Tarvittava kokonaisjäähdytysteho | Required total cooling capacity
|  | 194 | Patterimitoitus menoveden lämpötilan mukaan | Cooling coil dimensioning by inlet water temperature
|  | 195 | Patterimitoitus paluuveden lämpötilan mukaan | Cooling coil dimensioning by outlet water temperature
|  | 196 | Valitussa mallissa ei vesikiertoista lämmityspatteria | The selected model does not include a water-based heating coil.
|  | 197 | Valitussa mallissa ei vesikiertoista jäähdytyspatteria | The selected model does not include a water-based cooling coil.
|  | 198 | Huom. soveltuva alue | Value not applicable
|  | 199 | Valittu patterimalli soveltuu lämmitysvesille ~ | The selected coil model is suitable for heating water ~
|  | 200 | Valittu patterimalli soveltuu jäähdytysvesille ~ | The selected coil model is suitable for cooling water ~
|  | 201 | Huom. patterimitoitus onnistunut, kun laskelmassa ei ole virheilmoituksia. Muuta tarvittaessa meno- tai paluuveden lämpötiloja. | Note: Coil dimensioning is successful when there are no error messages in the calculation. Adjust the inlet or outlet water temperatures if necessary.
|  | 202 | * Ei valittuna säätöventtiiliä ja toimilaitetta / lämmitysryhmää | * No control valve or actuator / heating group selected.
|  | 203 | * Toimituksessa: Jälkilämmityksen 2-tieventtiili ja toimilaite - patterin 50/30 mukaan (kvs = 1,5). | * Included in the delivery: 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (kvs = 1.5).
|  | 204 | * Toimituksessa: Jälkilämmityksen pumppuryhmä 50/30 kasattuna ja eristettynä (kvs = 1,5). | * Included in the delivery: Post-heating pump unit for 50/30, assembled and insulated (kvs = 1.5).
|  | 205 | * Toimituksessa: Jälkilämmityksen 2-tieventtiili ja toimilaite - patterin 35/25 - 35/30 mukaan (kvs = 5,7). | * Included in the delivery: 2-way valve and actuator for post-heating, designed for a coil with 35/25 – 35/30 specifications (kvs = 5.7).
|  | 206 | * Toimituksessa: Jälkilämmityksen pumppuryhmä 35/25 - 35/30 kasattuna ja eristettynä (kvs = 5,7). | * Included in the delivery: Post-heating pump unit for 35/25 – 35/30, assembled and insulated (kvs = 5.7).
|  | 207 | * Ei valittuna säätöventtiiliä ja toimilaitetta / jäähdytysryhmää | * No control valve or actuator / cooling group selected.
|  | 208 | * Toimituksessa: Jäähdytyksen 3-tieventtiili ja toimilaite - patterin 7/12 - 10/15 mukaan (kvs = 4). | * Included in the delivery: 3-way valve and actuator for cooling, designed for a coil with 7/12 – 10/15 specifications (kvs = 4).
|  | 209 | * Toimituksessa: Jäähdytyksen pumppuryhmä 7/12 - 10/15 kasattuna ja eristettynä (kvs = 4). | * Included in the delivery: Cooling pump unit for 7/12 – 10/15, assembled and insulated (kvs = 4).
|  | 210 | * Toimituksessa: Jäähdytyksen 3-tieventtiili ja toimilaite - patterin 10/18 mukaan (kvs = 2,5). | * Included in the delivery: 3-way valve and actuator for cooling, designed for a coil with 10/18 specifications (kvs = 2.5).
|  | 211 | * Toimituksessa: Jäähdytyksen pumppuryhmä 10/18 kasattuna ja eristettynä (kvs = 2,5). | * Included in the delivery: Cooling pump unit for 10/18, assembled and insulated (kvs = 2.5).
|  | 212 | h / vrk | h / day
213
214
215
216
217
218
219
220
221
222

## SEC-laskenta (hidden)
SEC-laskenta
[6 empty] | SEC | -39.0477 |  |  |  | Vertailuarvo |  | -39.0477 | A
General typology | MISC |  | Valinta | MISC
Ducted units | 1.1 |  | 1 | 1.1 | [6 empty] | A+ |  | -42 | 0
Non-ducted units | 1.21 | [9 empty] | A | -42 | -34 | 0
[11 empty] | B | -34 | -26 | 0
Ventilation control | CTRL |  | Valinta | CTRL | [6 empty] | C | -26 | -23 | 0
Manual control (no DCV) | 1 |  | 4 | 0.65 | [6 empty] | D | -23 | -20 | 0
Clock control (no DCV) | 0.95 | [9 empty] | E | -20 | -10 | 0
Central demand control | 0.85 | [9 empty] | F | -10 | 0 | 0
Local demand control | 0.65 | [9 empty] | G | 0 |  | 0
Motor & drive | x-value |  | Valinta | x-value
On/off & single speed | 1 |  | 4 | 2
2-speed | 1.2
Multi-speed | 1.5
Variable-speed | 2
Climate | th | ΔTh | tdefr | ΔTdefr | Qdefr | Valinta | th | ΔTh | tdefr | ΔTdefr | Qdefr
Cold | 6552 | 14.5 | 1003 | 5.2 | 5.82 | 2 | 5112 | 9.5 | 168 | 2.4 | 0.45
Average | 5112 | 9.5 | 168 | 2.4 | 0.45
Warm | 4392 | 5
Defaults | Value
cair | 0.000344
qnet | 1.3
qref | 2.2
ta | 8760
pef | 2.5
ηh | 0.75
ηt | 0.797
SFP | 1.443 | kW/(m3/s)
SPI | 0.00040083 | kW/(m3/h)

## Laskenta tulopuoli 53mini (hidden)
| Tuloilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste
[8 empty] | 25 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
| y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 7 V |  | 6 V |  | 5V |  | 4V |  | 3V |  | 2V
| x = til.virta | [12 empty] | 22.2581 | -26.2532 | Ulko |  |  | ----> | Ulko | 45.3929 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
| 10V | [12 empty] | 22.2271 | -11.3304 | Tulo |  |  | ----> | Tulo | 60.2158 | dB |  |  | 25 | 95.3803 | 20 | 96.337 | 10 | 84.0396 | 10 | 69.5264 | 10 | 54.761 | 10 | 40.0158 | 8 | 25.9618 | 6 | 10.7762
| 2. aste polynomi | [23 empty] | 120 | 88.9477 | 50 | 93.1664 | 40 | 80.2259 | 25 | 67.2972 | 20 | 53.0568 | 20 | 37.7479 | 20 | 22.039 | 8 | 9.5218
| A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 83.7627 | 100 | 87.5448 | 60 | 77.5674 | 35 | 65.7582 | 40 | 49.4246 | 40 | 32.617 | 40 | 12.0085 | 10 | 8.3177
| -0.10916 | 5.3535 | 507.4949 | [10 empty] | 3-8.2 V | 6.3452 | -4.321 | 4.621 |  | ---> | Tulopuhallin | 4.621 | V | OK |  | 250 | 78.9265 | 150 | 81.3983 | 80 | 74.8033 | 55 | 62.5355 | 60 | 45.4157 | 50 | 29.6194 | 42 | 10.1699 | 12 | 7.1582
[14 empty] | 8.2 - 10V | 3.7673 | 16.818 | 2.1719 |  |  |  | TRUE |  |  |  | 320 | 72.6742 | 170 | 78.7554 | 100 | 71.9198 | 140 | 45.3908 | 120 | 28.6707 | 70 | 21.9159
| 8V | [18 empty] | Minimi qV | 10 | l/s |  |  | 370 | 67.6569 | 190 | 75.9846 | 200 | 54.9175 | 175 | 34.6092 | 125 | 26.4986
| A | B | C | [10 empty] | Polynomisovite teholle (3. aste) | [10 empty] | 450 | 58.105 | 330 | 49.8189 | 260 | 40.7241
| -0.06454 | 2.7688 | 352.2432 | [10 empty] | 0.00060408 | -0.0038652 | 0.32492 | 1.5497 |  | ----> | Tulopuhallin | 16.6957 | W | MAX
[20 empty] | Rajoitus | 16.6957 | W | 117 | W
7V
| A | B | C | [16 empty] | Poistopuhallin | 16.6551
| -0.053029 | 0.84444 | 313.5564 | [16 empty] | Elektroniikka | 4.4
| 6V | [12 empty] | Tarkistus, jos ei mittausalueella
| A | B | C | [10 empty] | Paine yli | 450 | Pa |  |  |  | Total power | 37.7508 | W
| -0.061286 | 1.6566 | 191.0751 | [10 empty] | Alfa yli | 0.25
| 5V | [18 empty] | Maks qV | 26.9444 | l/s
| A | B | C | [10 empty] | TRUE | [5 empty] | SFP | 1.4011 | kW/m3/s
| -0.067731 | 1.4348 | 134.5392
| 4V | [12 empty] | 13 | 141.7449
| A | B | C | [10 empty] | 15 | 140.8216
| -0.069131 | 0.96646 | 82.0233 | [10 empty] | 45 | 61.9492
| 3V | [17 empty] | Verkkokäyrän potenssikäyrän termi
| A | B | C | [15 empty] | alfa
| -0.07634 | 0.60529 | 43.7399 | [15 empty] | 0.16
| 2V | [36 empty] | 9 | 52.7857 | l/s
| A | B | C | [15 empty] | Verkkokäyrä mitoituspisteelle | [22 empty] | Tehostusvara
| 0.027027 | -2.1431 | 25.9557 | [15 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho |  |  |  | LwA |  |  | Ohjausjännite |  | Rajoitusalue
[19 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P |  | Vohj | l/s | Ulko | Tulo |  | V | l/s | V | l/s |  |  | Maksimi tehostusvara |  | Tarkistus onko käyttöalueella
[19 empty] | 10 | -0.10916 | 5.3535 | 507.4949 | -0.26916 | -34.6013 | 54.4906 | 95.3803 | 54.4906 | 475.0762 | 105.6532 |  | 10 | 54.4906 | 63.4487 | 77.9061 |  | 10 | 54.4906 | 10 | 54.4906 |  |  | 118% |  | TRUE | (OK, jos TOSI)
[19 empty] | 8 | -0.06454 | 2.7688 | 352.2432 | -0.22454 | -33.9187 | 46.2498 | 96.337 | 46.2498 | 342.2472 | 68.0251 |  | 7 | 40.3985 | 54.9586 | 70.2267 |  | 8 | 46.2498 | 8.2 | 47.7095 |  |  | Haluttu tehostuspiste |  | Tehostuspisteen ohjausjännite
[19 empty] | 7 | -0.053029 | 0.84444 | 313.5564 | -0.21303 | -36.4345 | 40.3985 | 84.0396 | 40.3985 | 261.1259 | 47.3233 |  | 6 | 33.3655 | 51.9214 | 66.7907 |  | 7 | 40.3985 |  |  |  |  | 27.5 | l/s | 5.015 | V
[19 empty] | 6 | -0.061286 | 1.6566 | 191.0751 | -0.22129 | -25.8793 | 33.3655 | 69.5264 | 33.3655 | 178.1209 | 31.7645 |  | 4 | 21.1464 | 41.9658 | 56.6198 |  | 6 | 33.3655 |  |  |  |  | 121 | Pa
[19 empty] | 5 | -0.067731 | 1.4348 | 134.5392 | -0.22773 | -21.3591 | 27.6595 | 54.761 | 27.6595 | 122.4073 | 20.1634 | [6 empty] | 5 | 27.6595
[19 empty] | 4 | -0.069131 | 0.96646 | 82.0233 | -0.22913 | -16.9285 | 21.1464 | 40.0158 | 21.1464 | 71.5471 | 12.2966 | [6 empty] | 4 | 21.1464
[19 empty] | 3 | -0.07634 | 0.60529 | 43.7399 | -0.23634 | -12.3837 | 14.9448 | 25.9618 | 14.9448 | 35.7355 | 7.1972 | [6 empty] | 3 | 14.9448
[19 empty] | 2 | 0.027027 | -2.1431 | 25.9557 | -0.13297 | -24.187 | 8.0703 | 22.039 | 8.0703 | 10.4207 | 4.4475 | [6 empty] | 2 | 8.0703
[19 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[22 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[19 empty] | Ulkokanava | 8.7 | 4.079 | 15 | 13 | 5 | -7 | -16 | -21 | -29 | -38 | ---> | 64.3929 | 58.3929 | 48.3929 | 38.3929 | 28.3929 | 21.3929 | 16.3929 | 21.3929 | 65.4622 | 45.7316 | OK
[20 empty] | 7 | 2.379 | 15 | 13 | 5 | -8 | -16 | -23 | -30 | -36
[20 empty] | 6 | 1.379 | 17 | 13 | 4 | -8 | -16 | -23 | -31 | -33
[20 empty] | 4 | 0.62098 | 19 | 13 | 3 | -7 | -17 | -24 | -29 | -24
[20 empty] | Valinta (lähin alue) | 0.62098 | 19 | 13 | 3 | -7 | -17 | -24 | -29 | -24
[19 empty] | Tulokanava | 8.7 | 4.079 | 9 | 8 | 5 | -4 | -9 | -12 | -17 | -25 | ----> | 74.2158 | 68.2158 | 63.2158 | 56.2158 | 54.2158 | 48.2158 | 39.2158 | 26.2158 | 75.549 | 60.3263 | OK
[20 empty] | 7 | 2.379 | 10 | 8 | 4 | -4 | -8 | -11 | -17 | -27
[20 empty] | 6 | 1.379 | 11 | 8 | 4 | -4 | -8 | -11 | -18 | -29 |  | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
[20 empty] | 4 | 0.62098 | 14 | 8 | 3 | -4 | -6 | -12 | -21 | -34
[20 empty] | Valinta (lähin alue) | 0.62098 | 14 | 8 | 3 | -4 | -6 | -12 | -21 | -34
Mitatut pisteet
| Ulkokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle
|  | l/s | LwA | P |  | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P |  | 2. aste polynomisovitus |  |  |  |  | Tilavuusvirran sovitteet, 2. aste polynomi | [5 empty] | Tehon sovitteet 2. aste polynomi
| 10V | 92.2089 | 61.2742 | 116.0686 |  | A | B |  |  |  | 10V | 92.5172 | 76.5244 | 116.3395 |  | A | B | C |  |  |  | A | B | C |  |  |  | A | B | C
|  | 85.9145 | 59.7882 | 115.8248 |  | 0.0071274 | -1.1069 | 102.6 |  |  |  | 85.9717 | 76.2299 | 115.9516 |  | 0.0026826 | -0.43053 | 93.4008 |  |  | 10 | -0.10916 | 5.3535 | 507.4949 |  |  | 10V | -0.0076626 | 1.4112 | 51.5093
|  | 77.6495 | 59.8823 | 114.7478 | [7 empty] | 77.4569 | 76.1353 | 115.1642 | [6 empty] | 8 | -0.06454 | 2.7688 | 352.2432 |  |  | 8V | 0.0023801 | 0.6488 | 32.9272
|  | 67.6198 | 60.2746 | 112.4328 | [7 empty] | 67.5429 | 76.563 | 112.3758 | [6 empty] | 7 | -0.053029 | 0.84444 | 313.5564 |  |  | 7V | 0.0025626 | 0.44127 | 25.3143
[21 empty] | 6 | -0.061286 | 1.6566 | 191.0751 |  |  | 6V | 0.00085293 | 0.42038 | 16.7888
| 8V | 78.0903 | 57.7695 | 75.0543 |  | A | B |  |  |  | 7V | 78.1262 | 72.5288 | 75.5493 |  | A | B | C |  |  | 5 | -0.067731 | 1.4348 | 134.5392 |  |  | 5V | 0.0018164 | 0.22382 | 12.5828
|  | 71.0543 | 56.6563 | 69.7367 |  | 0.0018813 | -0.14986 | 57.9424 |  |  |  | 71.063 | 71.9277 | 69.569 |  | 0.0010572 | -0.063788 | 71.0783 |  |  | 4 | -0.069131 | 0.96646 | 82.0233 |  |  | 4V | 0.0010897 | 0.16215 | 8.3804
|  | 61.6303 | 55.9636 | 63.0465 | [7 empty] | 61.2577 | 71.1026 | 62.6546 | [6 empty] | 3 | -0.07634 | 0.60529 | 43.7399 |  |  | 3V | 0.0015235 | 0.06474 | 5.8894
|  | 51.3416 | 55.1746 | 55.0229 | [7 empty] | 50.7792 | 70.5757 | 54.6988 | [6 empty] | 2 | 0.027027 | -2.1431 | 25.9557 |  |  | 2V | 0.0045541 | -0.04176 | 4.4879
| 6V | 66.5253 | 54.284 | 48.7175 |  | A | B | C |  |  | 6V | 66.0744 | 68.6757 | 48.2474 |  | A | B | C
|  | 60.7512 | 52.9352 | 44.7879 |  | 0.0039896 | -0.33048 | 58.5067 |  |  |  | 60.7366 | 68.0003 | 44.9096 |  | 0.0016435 | -0.10722 | 68.5384
|  | 51.5218 | 52.2166 | 40.7006 | [7 empty] | 51.0234 | 67.4017 | 40.4351
|  | 39.0624 | 51.6508 | 36.5041 | [7 empty] | 38.1074 | 66.8266 | 35.9366
| 4V | 39.2332 | 44.627 | 16.6553 |  | A | B | C |  |  | 4V | 39.476 | 58.1405 | 16.5974 |  | A | B | C
|  | 36.3879 | 42.8979 | 15.7297 |  | 0.015179 | -0.78209 | 51.7167 |  |  |  | 36.5288 | 57.7808 | 15.7356 |  | 0.0015744 | -0.013341 | 56.1978
|  | 31.6653 | 42.4578 | 14.7292 | [7 empty] | 31.3379 | 57.3447 | 14.6453
|  | 24.5528 | 41.6056 | 13.5193 | [7 empty] | 23.843 | 56.7708 | 13.3945
Mittausdata, lähde: "3797 Airfi Model 53mini - tilavuusvirtamittaukset - yhteenveto" -excel (Proj. 3797)
10V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 21.5555 | 1.7565 | 1.7565 | 579.7173 | -284.1356 | 295.603 | 579.7386 | 577.8874 | 79.8332 | 3613.3333 | 3.7036
| 30.7773 | 2.508 | 2.508 | 551.7767 | -304.6604 | 246.8266 | 551.4869 | 547.713 | 85.5084 | 3606.6667 | 2.7783
| 56.1882 | 4.5786 | 4.5786 | 482.6094 | -228.9441 | 253.65 | 482.5941 | 470.0158 | 106.708 | 3480 | 1.8991
| 62.1603 | 5.0653 | 5.0653 | 424.8316 | -209.8403 | 214.8967 | 424.737 | 409.3428 | 109.7788 | 3400 | 1.7661
| 68.5718 | 5.5877 | 5.5877 | 362.4261 | -165.4829 | 196.9161 | 362.399 | 343.6653 | 112.693 | 3333.3333 | 1.6434
| 74.1282 | 6.0405 | 6.0405 | 300.8789 | -120.5526 | 180.3514 | 300.9041 | 279.0114 | 114.0971 | 3246.6667 | 1.5392
| 78.5958 | 6.4046 | 6.4046 | 247.0781 | -98.3958 | 148.676 | 247.0718 | 222.4607 | 114.9999 | 3180 | 1.4632
| 83.2299 | 6.7822 | 6.7822 | 186.1593 | -59.3683 | 126.8007 | 186.1689 | 158.5701 | 115.7004 | 3126.6667 | 1.3901
| 87.798 | 7.1544 | 7.1544 | 127.6136 | -31.0249 | 96.5876 | 127.6126 | 96.9011 | 116.0096 | 3060 | 1.3213
| 92.3545 | 7.5257 | 7.5257 | 69.3931 | -3.8094 | 65.5779 | 69.3873 | 35.4055 | 116.1703 | 3013.3333 | 1.2579
| 97.3149 | 7.9299 | 7.9299 | 9.1021 | 36.335 | 45.4371 | 9.1021 | -28.6282 | 116.6543 | 2946.6667 | 1.1987
Lw-mittauksista | 92.5172 | [7 empty] | 116.3395
| 85.9717 | [7 empty] | 115.9516
| 77.4569 | [7 empty] | 115.1642
| 67.5429 | [7 empty] | 112.3758
8V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 17.3113 | 1.4107 | 1.4107 | 392.7682 | -179.5514 | 213.3018 | 392.8532 | 391.6593 | 46.318 | 3000 | 2.6756
| 25.4844 | 2.0767 | 2.0767 | 364 | -171.7949 | 192.2418 | 364.0367 | 361.4492 | 49.5371 | 2980 | 1.9438
| 52.398 | 4.2698 | 4.2698 | 325.644 | -147.3134 | 178.3462 | 325.6595 | 314.721 | 72.4422 | 2966.6667 | 1.3825
| 60.2735 | 4.9115 | 4.9115 | 283.5059 | -127.2852 | 156.2144 | 283.4996 | 269.0257 | 79.9232 | 2980 | 1.326
| 67.0919 | 5.4671 | 5.4671 | 246.5705 | -112.177 | 134.3621 | 246.5391 | 228.6053 | 87.9147 | 2973.3333 | 1.3104
| 74.2028 | 6.0466 | 6.0466 | 203.3695 | -77.7985 | 125.5709 | 203.3693 | 181.4326 | 94.9183 | 2973.3333 | 1.2792
| 79.5247 | 6.4803 | 6.4803 | 166.0288 | -54.2635 | 111.7684 | 166.032 | 140.8357 | 100.2589 | 2966.6667 | 1.2607
| 85.763 | 6.9886 | 6.9886 | 116.767 | -25.7536 | 91.0146 | 116.7683 | 87.464 | 106.8656 | 2973.3333 | 1.2461
| 91.4767 | 7.4542 | 7.4542 | 64.9832 | 6.7442 | 71.7299 | 64.9857 | 31.6467 | 112.6824 | 2986.6667 | 1.2318
| 97.1289 | 7.9148 | 7.9148 | 9.631 | 35.6333 | 45.2643 | 9.631 | -27.9552 | 116.7435 | 2960 | 1.2019
7V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 84.2267 | 6.8634 | 6.8634 | 8.3521 | 25.7251 | 34.0772 | 8.3521 | -19.9117 | 80.1288 | 2613.3333 | 0.95135
| 78.7879 | 6.4202 | 6.4202 | 50.7306 | 1.1556 | 51.8859 | 50.7304 | 25.9989 | 75.8741 | 2613.3333 | 0.96302
| 72.5664 | 5.9132 | 5.9132 | 96.0284 | -25.8829 | 70.1446 | 96.0275 | 75.0476 | 71.0229 | 2620 | 0.97873
| 65.9261 | 5.3721 | 5.3721 | 137.9856 | -47.6579 | 90.3325 | 137.9905 | 120.6745 | 65.9154 | 2633.3333 | 0.99984
| 58.5906 | 4.7744 | 4.7744 | 183.2564 | -74.4822 | 108.78 | 183.2622 | 169.5853 | 60.0329 | 2606.6667 | 1.0246
| 48.879 | 3.983 | 3.983 | 225.6218 | -103.1518 | 122.4672 | 225.6189 | 216.1003 | 52.7729 | 2606.6667 | 1.0797
| 38.5923 | 3.1448 | 3.1448 | 268.0587 | -127.4769 | 140.5812 | 268.0581 | 262.1243 | 44.8366 | 2606.6667 | 1.1618
| 15.0725 | 1.2282 | 1.2282 | 294.0578 | -132.9022 | 161.2099 | 294.1121 | 293.207 | 32.9828 | 2606.6667 | 2.1883
Lw-mittauksista | 78.1262 | [7 empty] | 75.5493
| 71.063 | [7 empty] | 69.569
| 61.2577 | [7 empty] | 62.6546
| 50.7792 | [7 empty] | 54.6988
6V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 13.401 | 1.092 | 1.092 | 207.8868 | -99.5875 | 108.3097 | 207.8972 | 207.1817 | 22.9949 | 2260 | 1.7159
| 24.4857 | 1.9953 | 1.9953 | 183.9014 | -94.0891 | 89.7989 | 183.8879 | 181.4993 | 26.306 | 2253.3333 | 1.0743
| 41.9597 | 3.4192 | 3.4192 | 156.8639 | -75.8201 | 81.0318 | 156.8519 | 149.8374 | 35.4396 | 2253.3333 | 0.84461
| 47.5812 | 3.8773 | 3.8773 | 134.0873 | -57.756 | 76.3303 | 134.0862 | 125.0663 | 38.3577 | 2240 | 0.80615
| 52.6622 | 4.2913 | 4.2913 | 108.7505 | -45.1773 | 63.5687 | 108.746 | 97.6968 | 41.3191 | 2246.6667 | 0.78461
| 57.121 | 4.6546 | 4.6546 | 84.9419 | -29.0411 | 55.8999 | 84.941 | 71.9416 | 43.6734 | 2246.6667 | 0.76458
| 62.683 | 5.1079 | 5.1079 | 54.7203 | -13.3833 | 41.3347 | 54.7179 | 39.0637 | 46.5384 | 2260 | 0.74244
| 67.0376 | 5.4627 | 5.4627 | 26.1792 | 5.9902 | 32.1693 | 26.1791 | 8.2743 | 48.9108 | 2246.6667 | 0.7296
| 70.0896 | 5.7114 | 5.7114 | 4.7068 | 18.9408 | 23.6476 | 4.7068 | -14.8654 | 50.6269 | 2253.3333 | 0.72232
Lw-mittauksista | 66.0744 | [7 empty] | 48.2474
| 60.7366 | [7 empty] | 44.9096
| 51.0234 | [7 empty] | 40.4351
| 38.1074 | [7 empty] | 35.9366
5V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 56.1087 | 4.5721 | 4.5721 | 3.0315 | 12.1805 | 15.212 | 3.0315 | -9.5112 | 30.6572 | 1913.3333 | 0.54639
| 52.6108 | 4.2871 | 4.2871 | 22.4382 | 0.0929 | 22.5309 | 22.438 | 11.4104 | 29.4273 | 1906.6667 | 0.55934
| 49.0229 | 3.9947 | 3.9947 | 41.8841 | -9.6122 | 32.2725 | 41.8847 | 32.3099 | 27.9977 | 1913.3333 | 0.57111
| 44.7321 | 3.6451 | 3.6451 | 61.984 | -23.1106 | 38.8727 | 61.9833 | 54.0112 | 26.4253 | 1873.3333 | 0.59075
| 40.1518 | 3.2719 | 3.2719 | 80.9543 | -34.1439 | 46.8097 | 80.9535 | 74.5304 | 24.6922 | 1920 | 0.61497
| 35.4281 | 2.8869 | 2.8869 | 100.5367 | -45.2381 | 55.298 | 100.5361 | 95.5354 | 22.7126 | 1906.6667 | 0.64109
| 29.9465 | 2.4403 | 2.4403 | 119.5592 | -54.6752 | 64.8861 | 119.5613 | 115.9884 | 20.6069 | 1893.3333 | 0.68812
| 11.1793 | 0.91097 | 0.91097 | 141.4652 | -70.3046 | 71.1602 | 141.4648 | 140.9669 | 15.3941 | 1886.6667 | 1.377
4V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 8.702 | 0.7091 | 0.7091 | 87.0023 | -44.2314 | 42.7695 | 87.0009 | 86.6992 | 9.9648 | 1520 | 1.1451
| 18.1387 | 1.4781 | 1.4781 | 71.6969 | -35.9916 | 35.7036 | 71.6952 | 70.3844 | 11.2859 | 1526.6667 | 0.6222
| 26.0925 | 2.1262 | 2.1262 | 63.1686 | -30.7016 | 32.4651 | 63.1667 | 60.4542 | 13.1527 | 1520 | 0.50408
| 31.4828 | 2.5655 | 2.5655 | 45.1815 | -16.2024 | 28.9804 | 45.1828 | 41.2339 | 14.4672 | 1520 | 0.45953
| 35.3992 | 2.8846 | 2.8846 | 30.1862 | -8.7261 | 21.4605 | 30.1866 | 25.1941 | 15.4572 | 1526.6667 | 0.43665
| 38.5762 | 3.1435 | 3.1435 | 15.7705 | -2.05 | 13.7204 | 15.7704 | 9.8416 | 16.211 | 1520 | 0.42023
| 41.6059 | 3.3904 | 3.3904 | 1.711 | 6.726 | 8.4371 | 1.711 | -5.1857 | 16.9533 | 1520 | 0.40747
Lw-mittauksista | 39.476 | [7 empty] | 16.5974
| 36.5288 | [7 empty] | 15.7356
| 31.3379 | [7 empty] | 14.6453
| 23.843 | [7 empty] | 13.3945
3V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 27.8071 | 2.2659 | 2.2659 | 1.5204 | 2.3374 | 3.8577 | 1.5204 | -1.5603 | 8.8598 | 1140 | 0.31862
| 25.1443 | 2.0489 | 2.0489 | 10.7406 | -4.2458 | 6.4945 | 10.7403 | 8.2214 | 8.4969 | 1140 | 0.33792
| 21.878 | 1.7828 | 1.7828 | 20.4173 | -8.0466 | 12.3707 | 20.4173 | 18.5103 | 8.026 | 1173.3333 | 0.36686
| 7.0716 | 0.57625 | 0.57625 | 44.2031 | -20.4775 | 23.7264 | 44.204 | 44.0047 | 6.4239 | 1140 | 0.9084
2V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 3.771 | 0.30729 | 0.30729 | 18.2583 | -8.6497 | 9.6087 | 18.2584 | 18.2018 | 4.3952 | 760 | 1.1655
| 7.6691 | 0.62493 | 0.62493 | 11.1099 | -5.9724 | 5.1374 | 11.1098 | 10.8754 | 4.4355 | 760 | 0.57836
| 14.4766 | 1.1797 | 1.1797 | 0.59527 | 0.56757 | 1.1628 | 0.59527 | -0.23969 | 4.8378 | 753.3333 | 0.33418

## Laskenta poistopuoli 53mini (hidden)
| Tuloilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste
[8 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
| y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 7 V |  | 6 V |  | 5V |  | 4V |  | 3V |  | 2V
| x = til.virta | [12 empty] | 19.5523 | -17.9094 | Poisto |  |  | ----> | Ulko | 46.4915 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
| 10V | [12 empty] | 21.6913 | -10.6612 | Jäte |  |  | ----> | Tulo | 60.7853 | dB |  |  | 15 | 103.5755 | 15 | 103.5643 | 10 | 98.8637 | 10 | 81.983 | 10 | 65.5083 | 10 | 48.7976 | 8 | 32.1988 | 5 | 16.0418
| 2. aste polynomi | [23 empty] | 120 | 94.8809 | 50 | 100.6899 | 40 | 94.8637 | 25 | 79.6966 | 20 | 63.6376 | 20 | 46.4153 | 20 | 28.017 | 10 | 13.0003
| A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 88.808 | 100 | 96.3124 | 60 | 92.0681 | 35 | 78.1228 | 40 | 59.6663 | 60 | 34.6466 | 40 | 18.1511 | 12 | 11.5272
| -0.037236 | -4.6867 | 899.8932 | [10 empty] | 3-8.6 V | 7.0209 | -3.8879 | 4.3915 |  | ---> | Tulopuhallin | 4.3915 | V | OK |  | 250 | 83.4021 | 150 | 91.5364 | 80 | 89.1541 | 55 | 74.8411 | 60 | 55.3137 | 80 | 25.6685 | 42 | 16.6658 | 14 | 9.7947
[14 empty] | 8.6 - 10V | 3.6413 | 23.1484 | 1.0425 |  |  |  | TRUE |  |  |  | 320 | 76.8313 | 170 | 89.487 | 100 | 86.1052 | 180 | 46.4366 | 120 | 37.8716 | 82 | 24.4583
| 8V | [18 empty] | Minimi qV | 10 | l/s |  |  | 370 | 71.942 | 190 | 87.3416 | 270 | 48.0489 | 200 | 38.257 | 125 | 35.793
| A | B | C | [10 empty] | Polynomisovite teholle | [10 empty] | 460 | 62.6626 | 360 | 60.282 | 280 | 43.7182
| -0.10408 | 9.0826 | 190.7117 | [10 empty] | 0.00031415 | 0.013424 | -0.13106 | 4.2956 |  | ----> | Tulopuhallin | 16.6551 | W | MAX
[20 empty] | Rajoitus | 16.6551 | W | 120.6 | W
7V
| A | B | C | [16 empty] | Tulopuhallin | 16.6957
| -0.050911 | 2.3628 | 274.0063 | [16 empty] | Elektroniikka | 4.4
| 6V | [12 empty] | Tarkistus, jos ei mittausalueella
| A | B | C | [10 empty] | Paine yli | 450 | Pa |  |  |  | Total power | 37.7508 | W
| -0.053455 | 2.0822 | 198.5776 | [10 empty] | Alfa yli | 0.25
| 5V | [18 empty] | Maks qV | 26.9444 | l/s
| A | B | C | [10 empty] | TRUE | [5 empty] | SFP | 1.4011 | kW/m3/s
| -0.052996 | 1.4985 | 139.2597
| 4V | [12 empty] | 13 | 149.7837
| A | B | C | [10 empty] | 15 | 149.8129
| -0.056451 | 1.1772 | 86.9774 | [10 empty] | 45 | 99.3749
| 3V | [17 empty] | Verkkokäyrän potenssikäyrän termi
| A | B | C | [15 empty] | alfa | [17 empty] | 9 | 59.2998 | l/s
| -0.059967 | 0.74137 | 46.3001 | [15 empty] | 0.13774
2V
| A | B | C | [15 empty] | Verkkokäyrä mitoituspisteelle | [22 empty] | Tehostusvara
| -0.063407 | 0.19754 | 18.1481 | [15 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho |  |  |  | LwA |  |  | Ohjausjännite |  | Rajoitusalue
[19 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P |  | Vohj | l/s | Poisto | Jäte |  | V | l/s | V | l/s |  |  | Maksimi tehostusvara |  | Tarkistus onko käyttöalueella
[19 empty] | 10 | -0.037236 | -4.6867 | 899.8932 | -0.17498 | -86.3467 | 59.5616 | 103.5755 | 59.5616 | 488.6461 | 110.6132 |  | 10 | 59.5616 | 61.3761 | 77.7442 |  | 10 | 59.5616 | 10 | 59.5616 |  |  | 121.1% |  | TRUE | (OK, jos TOSI)
[19 empty] | 8 | -0.10408 | 9.0826 | 190.7117 | -0.24182 | -15.0039 | 52.5626 | 103.5643 | 52.5626 | 380.5534 | 79.6168 |  | 7 | 44.8845 | 56.7733 | 72.1684 |  | 8 | 52.5626 | 8 | 52.279 |  |  | Haluttu tehostuspiste |  | Tehostuspisteen ohjausjännite
[19 empty] | 7 | -0.050911 | 2.3628 | 274.0063 | -0.18865 | -32.3597 | 44.8845 | 98.8637 | 44.8845 | 277.4947 | 54.6583 |  | 6 | 38.1295 | 54.1154 | 68.3834 |  | 7 | 44.8845 |  |  |  |  | 27.5 | l/s | 4.4707 | V
[19 empty] | 6 | -0.053455 | 2.0822 | 198.5776 | -0.1912 | -27.239 | 38.1295 | 81.983 | 38.1295 | 200.2551 | 35.8111 |  | 4 | 24.4105 | 44.0465 | 58.5102 |  | 6 | 38.1295 |  |  |  |  | 121 | Pa
[19 empty] | 5 | -0.052996 | 1.4985 | 139.2597 | -0.19074 | -23.3766 | 31.2329 | 65.5083 | 31.2329 | 134.3647 | 22.7615 | [6 empty] | 5 | 31.2329
[19 empty] | 4 | -0.056451 | 1.1772 | 86.9774 | -0.19419 | -18.3485 | 24.4105 | 48.7976 | 24.4105 | 82.0756 | 13.709 | [6 empty] | 4 | 24.4105
[19 empty] | 3 | -0.059967 | 0.74137 | 46.3001 | -0.19771 | -13.5426 | 17.2925 | 32.1988 | 17.2925 | 41.1885 | 7.7827 | [6 empty] | 3 | 17.2925
[19 empty] | 2 | -0.063407 | 0.19754 | 18.1481 | -0.20115 | -9.0202 | 10.0023 | 28.017 | 10.0023 | 13.7804 | 4.5894 | [6 empty] | 2 | 10.0023
[19 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[22 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[19 empty] | Poistokanava | 8.7 | 4.3085 | 12 | 12 | 6 | -7 | -13 | -25 | -35 | -41 | ---> | 62.4915 | 59.4915 | 50.4915 | 38.4915 | 34.4915 | 20.4915 | 14.4915 | 20.4915 | 64.4505 | 46.8138 | OK
[20 empty] | 7 | 2.6085 | 13 | 13 | 5 | -7 | -13 | -26 | -36 | -39
[20 empty] | 6 | 1.6085 | 16 | 13 | 5 | -8 | -12 | -26 | -37 | -36
[20 empty] | 4 | 0.39154 | 16 | 13 | 4 | -8 | -12 | -26 | -32 | -26
[20 empty] | Valinta (lähin alue) | 0.39154 | 16 | 13 | 4 | -8 | -12 | -26 | -32 | -26
[19 empty] | Jätekanava | 8.7 | 4.3085 | 8 | 7 | 4 | -2 | -7 | -11 | -17 | -25 | ----> | 72.7853 | 67.7853 | 62.7853 | 57.7853 | 55.7853 | 48.7853 | 39.7853 | 28.7853 | 74.4653 | 60.912 | OK
[20 empty] | 7 | 2.6085 | 10 | 7 | 4 | -3 | -7 | -11 | -18 | -26
[20 empty] | 6 | 1.6085 | 11 | 7 | 4 | -3 | -6 | -11 | -18 | -27 |  | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
[20 empty] | 4 | 0.39154 | 12 | 7 | 2 | -3 | -5 | -12 | -21 | -32
[20 empty] | Valinta (lähin alue) | 0.39154 | 12 | 7 | 2 | -3 | -5 | -12 | -21 | -32
Mitatut pisteet
| Poistokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle
|  | l/s | LwA | P |  | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P |  | 2. aste polynomisovitus |  |  |  |  | Tilavuusvirran sovitteet, 2. aste polynomi | [5 empty] | Tehon sovitteet 2. aste polynomi
| 10V | 98.7427 | 61.2655 | 116.2102 |  | A | B |  |  |  | 10V | 98.6525 | 77.9361 | 116.5275 |  | A | B | C |  |  |  | A | B | C |  |  |  | A | B | C
|  | 91.3072 | 62.2098 | 115.0322 |  | -0.001587 | 0.2524 | 51.973 |  |  |  | 91.6913 | 77.4445 | 116.1108 |  | 0.0019768 | -0.30797 | 89.0746 |  |  | 10 | -0.037236 | -4.6867 | 899.8932 |  |  | 10V | -0.0032525 | 0.6698 | 82.2574
|  | 82.8538 | 61.5993 | 113.8796 | [7 empty] | 81.2634 | 77.111 | 115.1164 | [6 empty] | 8 | -0.10408 | 9.0826 | 190.7117 |  |  | 8V | 0.001561 | 0.85768 | 30.2221
|  | 74.2419 | 62.0898 | 112.1219 | [7 empty] | 71.0536 | 77.1693 | 114.4051 | [6 empty] | 7 | -0.050911 | 2.3628 | 274.0063 |  |  | 7V | 0.0022193 | 0.58163 | 24.0812
[21 empty] | 6 | -0.053455 | 2.0822 | 198.5776 |  |  | 6V | 0.0020603 | 0.4132 | 17.0606
| 7V | 94.1901 | 59.7057 | 98.6619 |  | A | B |  |  |  | 7V | 93.6842 | 76.3735 | 97.1438 |  | A | B | C |  |  | 5 | -0.052996 | 1.4985 | 139.2597 |  |  | 5V | 0.0016455 | 0.29442 | 11.9608
|  | 84.0795 | 59.7968 | 86.6956 |  | -0.00040553 | 0.11941 | 52.2306 |  |  |  | 84.939 | 74.855 | 86.4837 |  | 0.0015614 | -0.13186 | 74.9412 |  |  | 4 | -0.056451 | 1.1772 | 86.9774 |  |  | 4V | 0.0009132 | 0.21348 | 7.9536
|  | 69.4354 | 58.2559 | 76.3687 | [7 empty] | 67.2367 | 73.2324 | 74.0709 | [6 empty] | 3 | -0.059967 | 0.74137 | 46.3001 |  |  | 3V | 0.0010529 | 0.1006 | 5.7282
|  | 53.7844 | 57.5719 | 66.9381 | [7 empty] | 48.914 | 72.1987 | 63.8733 | [6 empty] | 2 | -0.063407 | 0.19754 | 18.1481 |  |  | 2V | 0.0012053 | 0.032854 | 4.1402
| 6V | 78.2867 | 55.73 | 61.835 |  | A | B | C |  |  | 6V | 78.629 | 72.3052 | 62.7054 |  | A | B | C
|  | 70.1363 | 56.0622 | 55.1973 |  | 0.00062014 | -0.025388 | 54.1818 |  |  |  | 70.8618 | 70.9299 | 55.25 |  | 0.0019935 | -0.13696 | 70.7072
|  | 58.9213 | 54.3627 | 49.3948 | [7 empty] | 56.9533 | 69.4303 | 47.6317
|  | 45.7784 | 54.4498 | 43.3925 | [7 empty] | 41.8788 | 68.4518 | 41.7489
| 4V | 48.1024 | 45.557 | 20.5194 |  | A | B | C |  |  | 4V | 48.3085 | 61.3831 | 20.7948 |  | A | B | C
|  | 43.4026 | 45.2987 | 18.7945 |  | 0.0007618 | 0.0099978 | 43.3486 |  |  |  | 43.7426 | 60.3352 | 18.7283 |  | 0.0051381 | -0.25409 | 61.6511
|  | 37.0595 | 44.7037 | 17.429 | [7 empty] | 36.0478 | 59.1905 | 16.8103
|  | 28.9809 | 44.2938 | 15.6445 | [7 empty] | 26.8704 | 58.5275 | 15.2137
Mittausdata, lähde: "3797 Airfi Model 53mini - tilavuusvirtamittaukset - yhteenveto" -excel (Proj. 3797)
10V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 21.6145 | 1.7613 | 1.7613 | 584.8051 | -284.0844 | 300.7642 | 584.8486 | 582.9873 | 78.1463 | 3620 | 3.6155
| 52.9358 | 4.3136 | 4.3136 | 542.641 | -257.9152 | 284.7275 | 542.6427 | 531.4784 | 107.1717 | 3435 | 2.0246
| 60.1964 | 4.9052 | 4.9052 | 487.0272 | -228.18 | 258.8386 | 487.0186 | 472.5817 | 111.864 | 3333.3333 | 1.8583
| 66.85 | 5.4474 | 5.4474 | 424.3285 | -196.1718 | 228.1318 | 424.3036 | 406.4989 | 114.0523 | 3253.3333 | 1.7061
| 72.0925 | 5.8746 | 5.8746 | 367.9895 | -172.9109 | 195.0135 | 367.9243 | 347.2176 | 115.2055 | 3180 | 1.598
| 78.4302 | 6.3911 | 6.3911 | 304.8821 | -128.8659 | 176.0012 | 304.8671 | 280.3596 | 115.3346 | 3066.6667 | 1.4705
| 83.7057 | 6.821 | 6.821 | 245.9186 | -91.2775 | 154.6453 | 245.9228 | 218.0075 | 115.8917 | 2986.6667 | 1.3845
| 88.8509 | 7.2402 | 7.2402 | 184.4856 | -53.8141 | 130.6822 | 184.4964 | 153.0439 | 116.4306 | 2920 | 1.3104
| 94.3515 | 7.6885 | 7.6885 | 124.6798 | -17.844 | 106.8458 | 124.6898 | 89.2224 | 116.8817 | 2833.3333 | 1.2388
| 99.2468 | 8.0874 | 8.0874 | 66.7137 | 10.5365 | 77.2513 | 66.7148 | 27.4716 | 117.2773 | 2760 | 1.1817
| 104.325 | 8.5012 | 8.5012 | 9.7234 | 42.4721 | 52.1955 | 9.7234 | -33.6385 | 117.4445 | 2700 | 1.1258
LW-mittauksista | 98.7427 | [7 empty] | 116.2102
| 91.3072 | [7 empty] | 115.0322
| 82.8538 | [7 empty] | 113.8796
| 74.2419 | [7 empty] | 112.1219
| 98.6525 | [7 empty] | 116.5275
| 91.6913 | [7 empty] | 116.1108
| 81.2634 | [7 empty] | 115.1164
8V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 103.9417 | 8.4699 | 8.4699 | 11.9696 | 39.843 | 51.8126 | 11.9696 | -31.0743 | 116.7071 | 2706.6667 | 1.1228
| 100.5316 | 8.1921 | 8.1921 | 48.8105 | 18.7052 | 67.5154 | 48.8102 | 8.5443 | 116.505 | 2733.3333 | 1.1589
| 96.2376 | 7.8421 | 7.8421 | 94.5524 | -5.9032 | 88.6508 | 94.554 | 57.6544 | 116.1052 | 2806.6667 | 1.2064
| 91.8425 | 7.484 | 7.484 | 144.7222 | -39.5963 | 105.1182 | 144.7144 | 111.1083 | 115.9102 | 2853.3333 | 1.2621
| 88.3466 | 7.1991 | 7.1991 | 183.1988 | -59.2653 | 123.9295 | 183.1948 | 152.0983 | 115.624 | 2906.6667 | 1.3088
| 84.393 | 6.877 | 6.877 | 230.8534 | -80.5718 | 150.2943 | 230.8661 | 202.4906 | 115.0351 | 2946.6667 | 1.3631
| 77.5798 | 6.3218 | 6.3218 | 271.9414 | -109.2404 | 162.7027 | 271.9432 | 247.9643 | 108.0413 | 2960 | 1.3926
| 68.158 | 5.554 | 5.554 | 316.6869 | -139.4148 | 177.2651 | 316.6798 | 298.1716 | 96.6774 | 2973.3333 | 1.4184
| 57.0883 | 4.652 | 4.652 | 363.3149 | -170.9566 | 192.3374 | 363.294 | 350.3095 | 83.9289 | 2980 | 1.4702
| 45.8212 | 3.7338 | 3.7338 | 394.0235 | -179.1771 | 214.8934 | 394.0705 | 385.7055 | 71.262 | 2973.3333 | 1.5552
| 16.0325 | 1.3064 | 1.3064 | 402.7919 | -143.0647 | 260.034 | 403.0986 | 402.0745 | 44.8663 | 2973.3333 | 2.7985
7V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 15.7995 | 1.2875 | 1.2875 | 297.148 | -147.3176 | 149.8297 | 297.1473 | 296.1528 | 33.5965 | 2613.3333 | 2.1264
| 51.1288 | 4.1664 | 4.1664 | 267.0873 | -119.7948 | 147.3011 | 267.0959 | 256.6808 | 59.591 | 2622 | 1.1655
| 60.2455 | 4.9092 | 4.9092 | 232.4876 | -108.7816 | 123.6767 | 232.4583 | 217.9979 | 67.5552 | 2613.3333 | 1.1213
| 68.1914 | 5.5567 | 5.5567 | 197.4826 | -87.2295 | 110.2274 | 197.4568 | 178.9305 | 73.9379 | 2620 | 1.0843
| 74.926 | 6.1055 | 6.1055 | 163.4971 | -55.4362 | 108.0654 | 163.5016 | 141.1352 | 80.2549 | 2626.6667 | 1.0711
| 80.8151 | 6.5854 | 6.5854 | 129.5377 | -38.288 | 91.2463 | 129.5344 | 103.5138 | 86.0552 | 2613.3333 | 1.0648
| 86.1506 | 7.0202 | 7.0202 | 96.6635 | -17.3824 | 79.2795 | 96.6619 | 67.0922 | 91.1584 | 2613.3333 | 1.0581
| 93.7691 | 7.641 | 7.641 | 47.3808 | 12.1557 | 59.5352 | 47.3795 | 12.3486 | 99.2276 | 2620 | 1.0582
| 99.5303 | 8.1105 | 8.1105 | 9.2543 | 38.2667 | 47.521 | 9.2543 | -30.2135 | 105.493 | 2620 | 1.0599
| 94.1901 | [7 empty] | 98.6619
| 84.0795 | [7 empty] | 86.6956
| 69.4354 | [7 empty] | 76.3687
| 93.6842 | [7 empty] | 97.1438
| 84.939 | [7 empty] | 86.4837
| 67.2367 | [7 empty] | 74.0709
6V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 82.8102 | 6.748 | 6.748 | 7.2654 | 25.6797 | 32.9451 | 7.2654 | -20.0558 | 65.5624 | 2253.3333 | 0.79172
| 79.0197 | 6.4391 | 6.4391 | 29.7166 | 13.3286 | 43.0455 | 29.717 | 4.8398 | 62.8191 | 2246.6667 | 0.79498
| 75.0014 | 6.1117 | 6.1117 | 52.5758 | -0.11783 | 52.4592 | 52.577 | 30.1656 | 60.1381 | 2253.3333 | 0.80183
| 70.4723 | 5.7426 | 5.7426 | 78.2015 | -17.0802 | 61.1218 | 78.2021 | 58.4156 | 56.9197 | 2253.3333 | 0.80769
| 65.9877 | 5.3772 | 5.3772 | 102.5263 | -31.9446 | 70.5824 | 102.527 | 85.1787 | 53.0944 | 2253.3333 | 0.80461
| 60.5925 | 4.9375 | 4.9375 | 126.6565 | -43.1742 | 83.4899 | 126.664 | 112.0366 | 49.5191 | 2266.6667 | 0.81725
| 54.3911 | 4.4322 | 4.4322 | 151.5854 | -62.8884 | 88.697 | 151.5855 | 139.7989 | 45.6772 | 2253.3333 | 0.83979
| 49.0071 | 3.9935 | 3.9935 | 173.7123 | -76.1135 | 97.5994 | 173.7129 | 164.1443 | 42.3717 | 2253.3333 | 0.8646
| 40.7859 | 3.3235 | 3.3235 | 198.9291 | -91.5575 | 107.3733 | 198.9308 | 192.3033 | 37.1755 | 2253.3333 | 0.91148
| 13.9075 | 1.1333 | 1.1333 | 215.8747 | -104.5682 | 111.314 | 215.8822 | 215.1116 | 23.1607 | 2253.3333 | 1.6653
| 78.2867 | [7 empty] | 61.835
| 70.1363 | [7 empty] | 55.1973
| 58.9213 | [7 empty] | 49.3948
| 78.629 | [7 empty] | 62.7054
| 70.8618 | [7 empty] | 55.25
| 56.9533 | [7 empty] | 47.6317
5V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 11.3848 | 0.92772 | 0.92772 | 148.609 | -74.8264 | 73.7799 | 148.6064 | 148.09 | 15.5276 | 1893.3333 | 1.3639
| 34.5314 | 2.8139 | 2.8139 | 130.6361 | -61.0764 | 69.5578 | 130.6342 | 125.8835 | 24.0646 | 1893.3333 | 0.69689
| 41.4253 | 3.3756 | 3.3756 | 111.7404 | -51.2282 | 60.5075 | 111.7357 | 104.8988 | 27.1318 | 1893.3333 | 0.65496
| 47.2313 | 3.8488 | 3.8488 | 90.6437 | -34.6428 | 56.0022 | 90.645 | 81.7572 | 29.313 | 1893.3333 | 0.62063
| 51.7468 | 4.2167 | 4.2167 | 72.5602 | -25.9968 | 46.562 | 72.5588 | 61.8905 | 31.5393 | 1886.6667 | 0.60949
| 56.15 | 4.5755 | 4.5755 | 54.0759 | -14.6458 | 39.4291 | 54.0749 | 41.5137 | 33.892 | 1893.3333 | 0.6036
| 61.4984 | 5.0113 | 5.0113 | 31.5951 | 1.5518 | 33.1473 | 31.5955 | 16.5274 | 36.2832 | 1893.3333 | 0.58999
| 66.7279 | 5.4375 | 5.4375 | 5.082 | 16.3652 | 21.4471 | 5.0819 | -12.6578 | 38.8878 | 1900 | 0.58278
4V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 50.5941 | 4.1228 | 4.1228 | 2.9736 | 9.4239 | 12.3975 | 2.9736 | -7.2248 | 21.0953 | 1520 | 0.41695
| 47.1711 | 3.8438 | 3.8438 | 16.6696 | 1.2976 | 17.9672 | 16.6696 | 7.8045 | 19.9942 | 1520 | 0.42387
| 43.8063 | 3.5697 | 3.5697 | 30.0493 | -4.7614 | 25.2887 | 30.0501 | 22.4046 | 18.843 | 1520 | 0.43014
| 38.9749 | 3.176 | 3.176 | 45.5407 | -16.7465 | 28.7938 | 45.5403 | 39.4883 | 17.5995 | 1520 | 0.45156
| 34.2172 | 2.7883 | 2.7883 | 60.7247 | -27.1231 | 33.5999 | 60.723 | 56.0584 | 16.1883 | 1520 | 0.47311
| 29.2252 | 2.3815 | 2.3815 | 74.2978 | -32.2844 | 42.0146 | 74.299 | 70.8962 | 14.8088 | 1513.3333 | 0.50671
| 21.708 | 1.7689 | 1.7689 | 86.7524 | -37.6006 | 49.1565 | 86.757 | 84.8796 | 12.4502 | 1520 | 0.57353
| 8.8472 | 0.72094 | 0.72094 | 92.4728 | -43.7158 | 48.7599 | 92.4757 | 92.1639 | 10.0345 | 1526.6667 | 1.1342
| 48.1024 | [7 empty] | 20.5194
| 43.4026 | [7 empty] | 18.7945
| 37.0595 | [7 empty] | 17.429
| 28.9809 | [7 empty] | 15.6445
3V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 6.5509 | 0.53382 | 0.53382 | 48.5333 | -21.8901 | 26.6447 | 48.5348 | 48.3639 | 6.4301 | 1146.6667 | 0.98156
| 19.7072 | 1.6059 | 1.6059 | 37.8274 | -18.4792 | 19.3474 | 37.8267 | 36.2793 | 8.1253 | 1146.6667 | 0.4123
| 26.7535 | 2.1801 | 2.1801 | 23.1793 | -6.1593 | 17.0207 | 23.18 | 20.3284 | 9.193 | 1146.6667 | 0.34362
| 30.9895 | 2.5253 | 2.5253 | 11.2694 | -0.97456 | 10.2949 | 11.2694 | 7.4433 | 9.8072 | 1140 | 0.31647
| 34.3925 | 2.8026 | 2.8026 | 1.1587 | 4.6559 | 5.8146 | 1.1587 | -3.5539 | 10.4602 | 1153.3333 | 0.30414
2V
| qV (l/s) | v1 (m/s) | v2 (m/s) | Pd,kone,korj (Pa) | Ptot1 (Pa) | Ptot2 (Pa) | PfD (Pa) | PsfD (Pa) | P (W) | RPM (min-1) | SFP (kW/m3/s))
| 18.4906 | 1.5067 | 1.5067 | 0.1219 | 1.6722 | 1.7941 | 0.1219 | -1.2403 | 5.1597 | 760 | 0.27905
| 11.6239 | 0.9472 | 0.9472 | 11.8769 | -4.6178 | 7.2592 | 11.8771 | 11.3388 | 4.6849 | 766.6667 | 0.40304
| 4.8404 | 0.39443 | 0.39443 | 17.6181 | -6.3186 | 11.3001 | 17.6187 | 17.5254 | 4.3274 | 760 | 0.89402

## Laskenta poisto 53mini (hidden)
Tuloilma tilavuusvirta vs. painehäviö | [5 empty] | Syötä piste
[6 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [11 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V
x = til.virta | [11 empty] | 24.9897 | -36.459 | Ulko |  |  | ----> | Poisto | 45.8514 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 26.5243 | -28.8736 | Tulo |  |  | ----> | Jäte | 58.4915 | dB |  |  | 25 | 149.372 | 20 | 133.1733 | 15 | 99.9991 | 10 | 61.5554
2. aste polynomi | [22 empty] | 120 | 140.4402 | 50 | 128.5089 | 40 | 94.1082 | 20 | 57.8223
A | B | C | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 133.1231 | 100 | 120.2105 | 60 | 89.0698 | 30 | 53.8306
-0.06582 | 8.4394 | 232.9787 | [9 empty] | 4-9 V | 6.2279 | -0.26999 | 4.3697 |  | ---> | Poistopuhallin | 4.3697 | V | OK |  | 250 | 126.1684 | 150 | 111.0847 | 80 | 83.6755 | 35 | 51.7192
[12 empty] | 9 - 10V | 5.3732 | 6.6735 | 3.7726 |  |  |  | TRUE |  |  |  | 320 | 116.9093 | 170 | 107.1393 | 100 | 77.8371 | 80 | 25.8479
8 V | [17 empty] | Minimi qV | 20 | l/s |  |  | 390 | 105.6345 | 190 | 102.9859 | 185 | 42.1809
2. aste polynomi | [11 empty] | Polynomisovite teholle | [10 empty] | 460 | 89.8163 | 325 | 64.0021
A | B | C | [9 empty] | 0.067408 | -2.7549 | 39.9505 |  |  | ----> | Tulopuhallin | 14.6591 | W | MAX
-0.03135 | 1.7721 | 340 | [15 empty] | Rajoitus | 14.6591 | W | 168
6V | [17 empty] | Tulopuhallin | 16.6957
2. aste polynomi | [11 empty] | Tarkistus, jos ei mittausalueella | [5 empty] | Elektroniikka | 4.4
A | B | C | [9 empty] | Paine yli | 350 | Pa
-0.025105 | 0.62918 | 203.1282 | [9 empty] | Alfa yli | 0.32 |  |  |  |  | Total power | 35.7548 | W
4V | [11 empty] | TRUE | [5 empty] | Maks qV | 26.9444 | l/s
2. aste polynomi | [17 empty] | SFP | 1.327 | kW/m3/s
A | B | C | [9 empty] | 80 | 382.2937
-0.022467 | 0.0032873 | 94.9252 | [9 empty] | 90 | 354.5308
[12 empty] | 135 | 131.9295
9V lisämittaus
-0.039462 | 3.9323 | 320.2703 | [14 empty] | Verkkokäyrän potenssikäyrän termi
poistopuolen tilavuusviratmittaukset excelistä | [16 empty] | alfa
0.13774
[17 empty] | Verkkokäyrä mitoituspisteelle | [22 empty] | Tehostusvara
[17 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Järjestys muutettu
[17 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  | V | l/s |  |  |  |  | Maksimi tehostusvara |  | Tarkistus onko käyttöalueella
[17 empty] | 10 | -0.06582 | 8.4394 | 232.9787 | -0.20356 | -18.9471 | 60.4058 | 149.372 | 60.4058 | 502.5955 | 118.1345 | 64.3135 | 79.8521 |  | 10 | 60.4058 |  | 10 | 60.4058 |  |  |  |  | 124.2% |  | TRUE | (OK, jos TOSI)
[17 empty] | 8 | -0.03135 | 1.7721 | 340 | -0.16909 | -39.9065 | 50.3867 | 133.1733 | 50.3867 | 349.6983 | 68.6483 | 62.6189 | 75.9057 |  | 8 | 50.3867 |  | 9 | 55.0326 |  | 9 | 55.7813 | l/s | Haluttu tehostuspiste |  | Tehostuspisteen ohjausjännite
[17 empty] | 6 | -0.025105 | 0.62918 | 203.1282 | -0.16285 | -33.439 | 37.3027 | 99.9991 | 37.3027 | 191.6649 | 31.7412 | 55.7096 | 65.8484 |  | 6 | 37.3027 |  | 8 | 50.3867 |  |  |  |  | 29.6389 | l/s | 4.8024 | V
[17 empty] | 4 | -0.022467 | 0.0032873 | 94.9252 | -0.16021 | -24.3314 | 24.3519 | 61.5554 | 24.3519 | 81.6822 | 12.7085 | 42.1812 | 56.3206 |  | 4 | 24.3519 |  | 6 | 37.3027 |  |  |  |  | 121 | Pa
[17 empty] | 9 | -0.039462 | 3.9323 | 320.2703 | -0.1772 | -32.8418 | 55.0326 | 120 | 55.0326 | 417.1583 | 96.8542 |  |  |  | 9 | 55.0326 |  | 4 | 24.3519
[17 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[19 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[17 empty] | Poistokanava |  | 11 | 9 | 2 | -3 | -6 | -13 | -24 | -32 | ---> | 56.8514 | 54.8514 | 47.8514 | 42.8514 | 39.8514 | 32.8514 | 21.8514 | 13.8514 | 59.4544 | 45.88 | OK
[17 empty] | Jätekanava |  | 9 | 7 | 3 | -3 | -7 | -9 | -16 | -26 | ----> | 67.4915 | 65.4915 | 61.4915 | 55.4915 | 51.4915 | 49.4915 | 42.4915 | 32.4915 | 70.4793 | 58.73 | OK
[28 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[20 empty] | A | B | C
[19 empty] | 10V | -0.0030275 | 1.3879 | 45.3422
[19 empty] | 8V | -0.00069375 | 0.77076 | 31.5734
[19 empty] | 6V | 0.00076069 | 0.31459 | 18.9477
[19 empty] | 4V | 0.00085683 | 0.11014 | 9.5183
[19 empty] | 9V | 0.00099771 | 0.7768 | 51.0835
Mitatut pisteet
Poistokanava |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | Sovitteet 2. aste polynomi | [5 empty] | l/s | LwA | P |  | Sovitteet 2. aste polynomi | [5 empty] | l/s | W
10V | 142.3369 | 63.5048 | 168.3379 | A | B |  |  |  | 10V | 142.3109 | 76.3807 | 167.8298 |  | A | B | C |  |  | 10V | 145.9328 | 171.3366
| 135.5535 | 63.294 | 167.9612 | -9.1851e-05 | 0.007258 | 64.2102 |  |  |  | 135.753 | 75.6061 | 167.7629 |  | 0.0015813 | -0.36419 | 96.0815 |  |  |  | 141.0538 | 171.2048
| 120.8729 | 63.8585 | 167.8259 | [6 empty] | 121.885 | 75.2751 | 167.4385 | [7 empty] | 137.1494 | 170.5332
| 99.3543 | 64.0018 | 159.1945 | [6 empty] | 98.8459 | 75.5168 | 158.8284 | [7 empty] | 131.5549 | 170.8042
[20 empty] | 126.4531 | 170.4034
8V | 124.3962 | 60.7554 | 113.6032 | A | B |  |  |  | 8V | 124.3965 | 73.2742 | 113.3026 |  | A | B | C |  |  |  | 121.4682 | 169.7578
| 115.2858 | 59.8639 | 105.5586 | 0.0016134 | -0.30791 | 74.0374 |  |  |  | 115.28 | 72.0495 | 105.2986 |  | 0.002589 | -0.48814 | 93.9285 |  |  |  | 113.9745 | 167.399
| 101.6005 | 59.5003 | 97.9763 | [6 empty] | 101.9162 | 71.0791 | 97.7659 | [7 empty] | 98.8942 | 151.9457
| 86.8875 | 59.4372 | 86.9586 | [6 empty] | 83.8123 | 71.2005 | 86.7529 | [7 empty] | 82.5999 | 138.1508
[20 empty] | 59.6288 | 117.91
6V | 93.5096 | 54.4155 | 51.9634 | A | B | C |  |  | 6V | 93.746 | 66.5747 | 51.8407 |  | A | B | C |  |  |  | l/s | W
| 84.6032 | 53.4665 | 49.173 | 0.002663 | -0.37155 | 65.8638 |  |  |  | 83.8857 | 65.9002 | 49.0639 |  | 0.0019062 | -0.23534 | 71.9747 |  |  | 8V | 48.1138 | 66.9894
| 73.6372 | 52.9655 | 44.5872 | [6 empty] | 73.5289 | 64.7452 | 44.5202 | [7 empty] | 69.726 | 81.6244
| 62.441 | 53.0399 | 37.9588 | [6 empty] | 61.6046 | 64.7786 | 37.8969 | [7 empty] | 94.1458 | 99.9995
[20 empty] | 104.2146 | 103.4881
4V | 58.4401 | 45.0273 | 18.2887 | A | B | C |  |  | 4V | 58.4195 | 57.0409 | 18.2233 |  | A | B | C |  |  |  | 112.5722 | 108.2675
| 52.756 | 45.3909 | 17.1734 | -0.0038664 | 0.40538 | 34.6023 |  |  |  | 52.1969 | 56.4966 | 17.137 |  | 0.0031592 | -0.23928 | 60.2741 |  |  |  | 121.0832 | 114.1964
| 46.3831 | 44.9402 | 15.9765 | [6 empty] | 45.8921 | 55.8517 | 15.9708 | [7 empty] | 128.2598 | 120.0773
| 39.3321 | 44.6092 | 14.2864 | [6 empty] | 38.2254 | 55.7703 | 14.2532 | [7 empty] | l/s | W
[19 empty] | 6V | 95.2886 | 55.9264
[20 empty] | 84.2362 | 50.5993
[20 empty] | 67.2846 | 43.7967
[20 empty] | 38.7815 | 32.1103
[20 empty] | 28.1999 | 28.518
[20 empty] | l/s | W
[19 empty] | 4V | 18.2297 | 11.8293
[20 empty] | 38.3566 | 14.9067
[20 empty] | 50.652 | 17.4473
[20 empty] | 58.7134 | 18.8653
[20 empty] | l/s | W
[19 empty] | 9V | 120.1242 | 158.7186
[20 empty] | 104.2824 | 143.4085
[20 empty] | 70.6906 | 111.6079
[20 empty] | 49.5643 | 91.8764
[20 empty] | 88.6389 | 126.9145

## Laskenta vaipan läpi 53mini (hidden)
Ohjausjännite |  |  | Tarkistetaan onko rajoitetulla alueella
Tulo | 4.621 | V | 4.621 | V
Poisto | 4.3915 | V | 4.3915 | V
Sovite ohj. Jännite vs. LwA vaipan läpi
y = LwA, x = ohjausjännite
y = A*ln(x) + B | [8 empty] | Mittausdataa
[9 empty] | Vohj | LwA
| A | B | [6 empty] | 8.3 | 49.5539
4 V - 10 V | 22.8369 | 1.3011 | [6 empty] | 7 | 45.8079
[9 empty] | 6 | 42.2619
[9 empty] | 4 | 32.9249
Maksimi | 4.621 | V | ---> | 36.2554 | dB
Painotettu keskiarvo | 4.5445 | V | ---> | 35.8743 | dB
Korjaus
Äänitehotasot kanaviin | [8 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lw | LwA
Imupuoli | Ulko | 45.3929 | dB |  |  |  |  | 8.5-10 V | 62.653 | 60.5069 | 55.9401 | 43.0809 | 34.3487 | 28.4703 | 25.3526 | 22.918 | 65.2928 | 49.5539
| Poisto | 46.4915 | dB |  |  |  |  | 7 V | 59.9939 | 56.7887 | 51.825 | 39.2027 | 31.6371 | 24.9215 | 21.8683 | 18.3964 | 62.1446 | 45.8079
| Erotus | 1.0986 | dB |  |  |  |  | 6 V | 56.8505 | 54.179 | 47.8647 | 35.7355 | 28.8401 | 21.5733 | 16.448 | 12.649 | 59.0948 | 42.2619
[8 empty] | 4 V | 51.6081 | 44.637 | 37.3301 | 25.7994 | 20.3219 | 12.1999 | 7.391 | 5.1413 | 52.5484 | 32.9249
Painepuoli | Tulo | 60.2158 | dB
| Jäte | 60.7853 | dB | [5 empty] | 13.0992 | 10.9531 | 6.3863 | -6.473 | -15.2052 | -21.0836 | -24.2012 | -26.6358
| Erotus | 0.56953 | dB | [5 empty] | 14.186 | 10.9808 | 6.0171 | -6.6052 | -14.1708 | -20.8865 | -23.9396 | -27.4115
[9 empty] | 14.5886 | 11.9171 | 5.6028 | -6.5264 | -13.4218 | -20.6886 | -25.8139 | -29.6129
Keskiarvo erotus | 0.83409 | dB | [6 empty] | 18.6831 | 11.7121 | 4.4051 | -7.1256 | -12.603 | -20.725 | -25.5339 | -27.7836
Korjaus K | 4.5761 | dB | [5 empty] | KA | 15.1392 | 11.3908 | 5.6028 | -6.6825 | -13.8502 | -20.8459 | -24.8722 | -27.861 |  | tarkistus
[8 empty] | KA pyör | 15 | 11 | 6 | -7 | -14 | -21 | -25 | -28 |  | 0.35598 | OK
Taustamelukorjattu | 40.8315 | dB
Maksimikorjaus | 33.6554 | dB
|  |  |  | LpA10m2 | LpA2,5m2
Valinta | 35.8743 | dB |  | 30.3949 | 36.4155
VK korjaus | -1.5 | dB
Total | 34.3743 | dB
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 15 | 11 | 6 | -7 | -14 | -21 | -25 | -28 | ---> | 49.3743 | 45.3743 | 40.3743 | 27.3743 | 20.3743 | 13.3743 | 9.3743 | 6.3743 | 51.2268 | 34.7303 |  | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
| Tulopuoli |  |  |  |  | Poistopuoli |  |  |  |  | P* [W] | Äänitehotasot oktaavikaistoittain LW,okt [dB] | [7 empty] | LW,kok** [dB] | LW,A,kok** [dB]
| Uohj [V] | qV [dm3/s] | ps11 [Pa] | ps12 [Pa] | ptU [Pa] | Uohj [V] | qV [dm3/s] | ps11 [Pa] | ps12 [Pa] | ptU [Pa] |  | 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz | [5 empty] | VK
[23 empty] | qV | Ptu | alfa
| 9.9943 | 92.737 | -47.582 | 19.7243 | 67.3062 | 9.9943 | 98.8097 | -61.2288 | 12.3188 | 73.5476 | 227.6163 | 61.2768 | 59.9436 | 55.6741 | 43.6763 | 35.1752 | 28.1857 | 24.5369 | 21.9134 | 64.3551 | 49.3747 |  | 95.7733 | 70.4269 | 0.007678 | 49.3747
| 9.997 | 85.4081 | -80.2034 | 82.9146 | 163.1179 | 9.997 | 91.0781 | -85.9305 | 78.9222 | 164.8527 | 226.8103 | 62.7921 | 60.1711 | 55.941 | 42.9308 | 34.4782 | 28.1417 | 25.0054 | 22.7068 | 65.2615 | 49.4894 |  | 88.2431 | 163.9853 | 0.021059 | 49.4894
| 9.9959 | 76.6831 | -132.6424 | 135.1846 | 267.827 | 9.9959 | 81.745 | -135.9161 | 131.893 | 267.8091 | 225.3471 | 63.3992 | 60.8204 | 55.8996 | 42.751 | 33.9456 | 28.5902 | 25.633 | 22.9248 | 65.8057 | 49.5541 |  | 79.2141 | 267.818 | 0.042681 | 49.5541
| 9.9913 | 66.8517 | -190.4476 | 185.9406 | 376.3882 | 9.9913 | 71.6761 | -191.3799 | 180.2656 | 371.6455 | 222.485 | 62.8715 | 61.0039 | 56.228 | 42.9043 | 33.6364 | 28.9167 | 26.0766 | 23.8957 | 65.611 | 49.7867 |  | 69.2639 | 374.0168 | 0.077961 | 49.7867
| 6.993 | 79.2675 | -34.741 | 14.78 | 49.521 | 6.993 | 93.6869 | -53.5679 | 10.735 | 64.3028 | 170.1219 | 60.3956 | 57.9124 | 52.927 | 40.809 | 33.12 | 25.8406 | 21.7479 | 19.2825 | 62.8435 | 47.0246 |  | 86.4772 | 56.9119 | 0.0076103 | 47.0246 | 1.2167
| 6.995 | 70.5191 | -55.447 | 56.2562 | 111.7032 | 6.995 | 84.0764 | -68.351 | 63.1985 | 131.5495 | 152.7923 | 60.9509 | 57.0532 | 52.299 | 39.4452 | 32.4328 | 25.4055 | 24.0571 | 18.6477 | 62.8627 | 46.2544 |  | 77.2977 | 121.6264 | 0.020356 | 46.2544 | 0.44645
| 6.994 | 60.4895 | -84.5581 | 84.62 | 169.1781 | 6.994 | 68.1971 | -97.5379 | 95.7618 | 193.2997 | 134.3845 | 59.6713 | 56.2216 | 51.2329 | 38.5498 | 30.8905 | 24.2298 | 20.476 | 17.9454 | 61.7252 | 45.1548 |  | 64.3433 | 181.2389 | 0.043777 | 45.1548 | -0.65313
| 6.993 | 50.5361 | -111.1574 | 106.7394 | 217.8968 | 6.993 | 50.7257 | -124.3351 | 118.1024 | 242.4375 | 116.5379 | 58.6162 | 55.6216 | 50.4183 | 37.2282 | 29.0403 | 23.9179 | 19.973 | 17.4959 | 60.823 | 44.3084 |  | 50.6309 | 230.1672 | 0.089787 | 44.3084 | -1.4995
| 5.9954 | 66.662 | -24.5871 | 10.8608 | 35.4479 | 5.9954 | 77.9057 | -37.6675 | 7.7908 | 45.4583 | 107.7147 | 57.6162 | 54.9822 | 49.0455 | 37.163 | 29.113 | 22.3201 | 16.9586 | 13.7265 | 59.9081 | 43.3768 |  | 72.2839 | 40.4531 | 0.0077423 | 43.3768 | 1.1148
| 5.996 | 60.3068 | -39.8998 | 39.4548 | 79.3546 | 5.996 | 70.2592 | -48.3685 | 45.0841 | 93.4526 | 97.4829 | 56.9818 | 54.1883 | 48.1893 | 35.934 | 28.3111 | 21.1077 | 16.7325 | 12.4322 | 59.2018 | 42.452 |  | 65.283 | 86.4036 | 0.020274 | 42.452 | 0.19013
| 5.996 | 50.5573 | -59.5657 | 59.2133 | 118.779 | 5.996 | 57.7389 | -69.2915 | 68.7698 | 138.0613 | 86.5148 | 56.8553 | 53.7546 | 47.4438 | 35.477 | 30.6182 | 22.0477 | 16.3176 | 12.2394 | 58.9352 | 41.937 |  | 54.1481 | 128.4201 | 0.043799 | 41.937 | -0.32495
| 5.995 | 38.4384 | -79.0254 | 75.3993 | 154.4246 | 5.995 | 43.8584 | -89.3249 | 84.6476 | 173.9725 | 76.6751 | 55.7458 | 53.6623 | 46.3302 | 33.6727 | 26.1949 | 20.5968 | 15.6757 | 11.9794 | 58.154 | 40.9229 |  | 41.1484 | 164.1986 | 0.096976 | 40.9229 | -1.339
| 3.996 | 39.7609 | -8.7517 | 4.1969 | 12.9485 | 3.996 | 47.8718 | -13.8567 | 3.2799 | 17.1366 | 35.6231 | 51.833 | 45.3695 | 38.7619 | 25.9341 | 19.5498 | 11.452 | 7.152 | 3.7444 | 52.8995 | 33.7506 |  | 43.8164 | 15.0426 | 0.0078352 | 33.7506 | 0.8257
| 3.996 | 36.524 | -15.307 | 14.4043 | 29.7114 | 3.996 | 43.5168 | -18.4735 | 18.2548 | 36.7283 | 33.2035 | 52.2675 | 44.7237 | 36.8049 | 26.7952 | 23.2089 | 13.5751 | 8.0027 | 5.5036 | 53.0909 | 33.1712 |  | 40.0204 | 33.2198 | 0.020741 | 33.1712 | 0.24626
| 3.996 | 31.5041 | -23.2778 | 22.2188 | 45.4966 | 3.996 | 36.6753 | -27.1943 | 27.5766 | 54.7709 | 30.579 | 51.3167 | 44.6364 | 37.5036 | 24.4505 | 16.9324 | 11.7085 | 7.6225 | 5.5842 | 52.3167 | 32.7108 |  | 34.0897 | 50.1337 | 0.04314 | 32.7108 | -0.21415
| 3.995 | 24.7185 | -31.6331 | 29.3368 | 60.9699 | 3.995 | 29.0401 | -35.8321 | 33.7152 | 69.5474 | 27.9906 | 50.8908 | 43.6477 | 35.6718 | 25.7017 | 19.134 | 11.7068 | 6.6728 | 5.4783 | 51.7637 | 31.848 |  | 26.8793 | 65.2586 | 0.090324 | 31.848 | -1.077
[11 empty] | 10 | 62.653 | 60.5069 | 55.9401 | 43.0809 | 34.3487 | 28.4703 | 25.3526 | 22.918 | 65.2928 | 49.5539
[11 empty] | 7 | 59.9939 | 56.7887 | 51.825 | 39.2027 | 31.6371 | 24.9215 | 21.8683 | 18.3964 | 62.1446 | 45.8079
[11 empty] | 6 | 56.8505 | 54.179 | 47.8647 | 35.7355 | 28.8401 | 21.5733 | 16.448 | 12.649 | 59.0948 | 42.2619
[11 empty] | 4 | 51.6081 | 44.637 | 37.3301 | 25.7994 | 20.3219 | 12.1999 | 7.391 | 5.1413 | 52.5484 | 32.9249
Verkkokäyrän korjaus
[20 empty] | -0.94214 | -3.4497
[20 empty] | l/s | 25.9722
[20 empty] | Pa | 100
[20 empty] | alfa | 0.14825
[20 empty] | Korjaus | -1.6512 | dB
[20 empty] | Yli 7.5 V | 0
[20 empty] | Tarkistus | -1.6512 | dB
[20 empty] | MAX | 1.5
[20 empty] | MIN | -1.5
[20 empty] | Rajoitus | -1.5 | dB

## Laskenta tulopuoli 130 (hidden)
Tuloilma tilavuusvirta vs. painehäviö | [5 empty] | Syötä piste
[6 empty] | 25 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [11 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V
x = til.virta | [11 empty] | 21.7094 | -25.1681 | Ulko |  |  | ----> | Ulko | 44.7116 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 23.0045 | -14.6488 | Tulo |  |  | ----> | Tulo | 59.3997 | dB |  |  | 25 | 131.6515 | 20 | 116.8545 | 10 | 86.0149 | 10 | 49.4817
2. aste polynomi | [22 empty] | 120 | 122.5295 | 50 | 112.3072 | 40 | 78.9504 | 20 | 45.3946
A | B | C | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 115.0427 | 100 | 104.2194 | 60 | 73.9658 | 25 | 43.2863
-0.064092 | 5.8765 | 362.1923 | [9 empty] | 4-9V | 6.1526 | -3.3141 | 4.602 |  | ---> | Tulopuhallin | 4.602 | V | OK |  | 250 | 107.9109 | 150 | 95.3292 | 80 | 68.7211 | 30 | 41.1311
Lähde: 3478 Airfi Model-130 tilavuusvirtamittaukset tuloopuhallin.xslx | [11 empty] | 9 - 10V | 3.3256 | 22.1429 | 0.85913 |  |  |  | TRUE |  |  |  | 320 | 98.3807 | 170 | 91.4873 | 100 | 63.171 | 70 | 21.6983
8V | [17 empty] | Minimi qV | 20 | l/s |  |  | 390 | 86.684 | 190 | 87.4442 | 180 | 36.2552
2. aste polynomi | [11 empty] | Polynomisovite teholle | [10 empty] | 460 | 69.8377 | 320 | 51.7322
A | B | C | [9 empty] | 0.066273 | -2.2356 | 30.4222 |  |  | ----> | Tulopuhallin | 15.9533 | W | MAX
-0.032862 | 0.93338 | 359.6602 | [15 empty] | Rajoitus | 15.9533 | W | 168 | W
6V | [17 empty] | Poistopuhallin | 14.6591
2. aste polynomi | [17 empty] | Elektroniikka | 4.4
A | B | C | [9 empty] | Tarkistus, jos ei mittausalueella
-0.019444 | -1.039 | 243.2262 | [9 empty] | Paine yli | 350 | Pa |  |  |  | Total power | 35.0124 | W
[12 empty] | Alfa yli | 0.45
4V | [17 empty] | Maks qV | 26.9444 | l/s
2. aste polynomi | [11 empty] | TRUE | [5 empty] | SFP | 1.2994 | kW/m3/s
A | B | C
-0.012117 | -1.2971 | 103.8491 | [9 empty] | 60 | 412.9607
[12 empty] | 90 | 294.8886
9V lisämittaus | [11 empty] | 120 | 115.1558
-0.034256 | 1.2027 | 464.1223 | [14 empty] | Verkkokäyrän potenssikäyrän termi
alfa
0.16
[17 empty] | Verkkokäyrä mitoituspisteelle | [22 empty] | Tehostusvara
[17 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Järjestys muutettu
[17 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  | V | l/s |  |  |  |  | Maksimi tehostusvara |  | Tarkistus onko käyttöalueella
[17 empty] | 10 | -0.064092 | 5.8765 | 362.1923 | -0.22409 | -29.1751 | 55.3988 | 131.6515 | 55.3988 | 491.0451 | 112.3712 | 61.9932 | 77.6272 |  | 10 | 55.3988 |  | 10 | 55.3988 |  |  |  |  | 121.6% |  | TRUE | (OK, jos TOSI)
[17 empty] | 8 | -0.032862 | 0.93338 | 359.6602 | -0.19286 | -40.8319 | 45.6716 | 116.8545 | 45.6716 | 333.7425 | 66.9478 | 57.9688 | 73.45 |  | 8 | 45.6716 |  | 9 | 52.0732 |  | 9 | 52.0589 | l/s | Haluttu tehostuspiste |  | Tehostuspisteen ohjausjännite
[17 empty] | 6 | -0.019444 | -1.039 | 243.2262 | -0.17944 | -39.8249 | 34.035 | 86.0149 | 34.035 | 185.3411 | 32.0151 | 51.1109 | 66.3486 |  | 6 | 34.035 |  | 8 | 45.6716 |  |  |  |  | 27.5 | l/s | 5.0083 | V
[17 empty] | 4 | -0.012117 | -1.2971 | 103.8491 | -0.17212 | -28.6187 | 21.0828 | 49.4817 | 21.0828 | 71.1175 | 12.3941 | 41.1274 | 55.5166 |  | 4 | 21.0828 |  | 6 | 34.035 |  |  |  |  | 121 | Pa
[17 empty] | 9 | -0.034256 | 1.2027 | 464.1223 | -0.19426 | -45.8821 | 52.0732 | 120 | 52.0732 | 433.8597 | 90.3646 |  |  |  | 9 | 52.0732 |  | 4 | 21.0828
[17 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
muutettu käsin
[19 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[17 empty] | Ulkokanava |  | 14 | 11 | 4 | -3 | -11 | -17 | -25 | -34 | ---> | 58.7116 | 55.7116 | 48.7116 | 41.7116 | 33.7116 | 27.7116 | 19.7116 | 10.7116 | 60.8208 | 44.9889 | OK
[17 empty] | Tulokanava |  | 10 | 9 | 2 | -3 | -8 | -9 | -15 | -25 | ----> | 69.3997 | 68.3997 | 61.3997 | 56.3997 | 51.3997 | 50.3997 | 44.3997 | 34.3997 | 72.485 | 59.5882 | OK
[28 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[20 empty] | A | B | C
[19 empty] | 10V | -0.0034237 | 1.5422 | 37.4433
[19 empty] | 8V | 0.00094672 | 0.6572 | 34.9576
[19 empty] | 6V | 0.00089726 | 0.36354 | 18.6025
[19 empty] | 4V | 0.00064187 | 0.15621 | 8.8154
[19 empty] | 9V | 0.0020751 | 0.46878 | 60.3268
Mitatut pisteet
Ulkokanava |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P |  | 2. aste polynomisovitus | [5 empty] | l/s | W
10V | 124.4555 | 59.4642 | 165.992 | A | B |  |  |  | 10V | 124.4983 | 74.8437 | 165.8695 |  | A | B | C |  |  | 10V | 126.5463 | 166.5755
| 116.5172 | 59.362 | 165.8456 | 0.00029785 | -0.091487 | 66.1474 |  |  |  | 116.2287 | 74.9871 | 166.2914 |  | 4.3618e-05 | -0.048971 | 80.2063 |  |  |  | 124.1742 | 167.9762
| 101.7053 | 60.0279 | 165.4094 | [6 empty] | 102.7316 | 75.709 | 165.8539 | [7 empty] | 119.5168 | 166.9898
| 82.365 | 60.6082 | 141.333 | [6 empty] | 82.099 | 76.4649 | 140.67 | [7 empty] | 115.0733 | 167.559
[20 empty] | 110.3771 | 166.8307
8V | 108.6161 | 56.8143 | 113.8836 | A | B |  |  |  | 8V | 108.799 | 72.0001 | 113.0368 |  | A | B | C |  |  |  | 103.2997 | 163.1785
| 98.2815 | 56.0959 | 105.6018 | 0.001565 | -0.26008 | 66.5828 |  |  |  | 97.1597 | 71.6388 | 105.3675 |  | 0.00086769 | -0.15748 | 78.8326 |  |  |  | 92.0097 | 149.0289
| 84.2379 | 55.8124 | 96.7263 | [6 empty] | 85.2277 | 71.7818 | 97.1253 | [7 empty] | 79.6479 | 137.7006
| 68.2262 | 56.1136 | 80.4859 | [6 empty] | 67.1192 | 72.1559 | 80.1291 | [7 empty] | 68.4189 | 126.9501
[20 empty] | 52.8805 | 109.7592
6V | 78.9187 | 50.3545 | 50.8363 | A | B | C |  |  | 6V | 79.1899 | 65.345 | 50.707 |  | A | B | C |  |  |  | l/s | W
| 70.5802 | 49.7164 | 47.0694 | 0.0027429 | -0.3263 | 59.0392 |  |  |  | 69.2918 | 65.1911 | 46.9974 |  | 0.0010734 | -0.14376 | 69.9982 |  |  | 8V | 42.2113 | 64.5732
| 61.0032 | 49.3032 | 42.9784 | [6 empty] | 61.0722 | 65.2214 | 43.1415 | [7 empty] | 58.6429 | 76.6972
| 50.0093 | 49.5919 | 35.9224 | [6 empty] | 48.9757 | 65.5322 | 35.8208 | [7 empty] | 71.8972 | 86.4689
[20 empty] | 89.0523 | 101.3483
4V | 47.2096 | 41.2636 | 17.2151 | A | B | C |  |  | 4V | 47.4828 | 55.8266 | 17.306 |  | A | B | C |  |  |  | 97.5877 | 108.3315
| 42.4654 | 40.7522 | 16.0235 | 0.0028608 | -0.19238 | 43.9119 |  |  |  | 41.2285 | 55.9301 | 16.0948 |  | -0.00079728 | 0.067108 | 54.4561 |  |  |  | 104.2713 | 114.3027
| 37.1028 | 40.8292 | 14.7079 | [6 empty] | 36.4752 | 55.7886 | 14.9632 | [7 empty] | 111.7428 | 119.6129
| 29.1826 | 40.7074 | 13.1825 | [6 empty] | 27.6648 | 55.7131 | 13.3557 | [7 empty] | l/s | W
[19 empty] | 6V | 81.1988 | 53.9486
[20 empty] | 70.2545 | 48.7624
[20 empty] | 52.8511 | 40.1748
[20 empty] | 35.4279 | 32.6546
[20 empty] | 24.9809 | 28.2437
[20 empty] | l/s | W
[19 empty] | 4V | 11.7114 | 10.7253
[20 empty] | 27.8186 | 13.6997
[20 empty] | 36.0466 | 15.2306
[20 empty] | 46.4714 | 17.4763
[20 empty] | l/s | W
[19 empty] | 9V | 141.104 | 167.9366
[20 empty] | 124.949 | 151.2016
[20 empty] | 106.6222 | 133.5089
[20 empty] | 64.4199 | 99.092
[20 empty] | 56.2297 | 93.1148
[20 empty] | 83.6112 | 114.5452
Tehodatat tilavuusvirtamittauksista

## Laskenta poistopuoli 130 (hidden)
Tuloilma tilavuusvirta vs. painehäviö | [5 empty] | Syötä piste
[6 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [11 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V
x = til.virta | [11 empty] | 24.9897 | -36.459 | Ulko |  |  | ----> | Poisto | 45.8514 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 26.5243 | -28.8736 | Tulo |  |  | ----> | Jäte | 58.4915 | dB |  |  | 25 | 149.372 | 20 | 133.1733 | 15 | 99.9991 | 10 | 61.5554
2. aste polynomi | [22 empty] | 120 | 140.4402 | 50 | 128.5089 | 40 | 94.1082 | 20 | 57.8223
A | B | C | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 133.1231 | 100 | 120.2105 | 60 | 89.0698 | 30 | 53.8306
-0.06582 | 8.4394 | 232.9787 | [9 empty] | 4-9 V | 6.2279 | -0.26999 | 4.3697 |  | ---> | Poistopuhallin | 4.3697 | V | OK |  | 250 | 126.1684 | 150 | 111.0847 | 80 | 83.6755 | 35 | 51.7192
[12 empty] | 9 - 10V | 5.3732 | 6.6735 | 3.7726 |  |  |  | TRUE |  |  |  | 320 | 116.9093 | 170 | 107.1393 | 100 | 77.8371 | 80 | 25.8479
8 V | [17 empty] | Minimi qV | 20 | l/s |  |  | 390 | 105.6345 | 190 | 102.9859 | 185 | 42.1809
2. aste polynomi | [11 empty] | Polynomisovite teholle | [10 empty] | 460 | 89.8163 | 325 | 64.0021
A | B | C | [9 empty] | 0.067408 | -2.7549 | 39.9505 |  |  | ----> | Tulopuhallin | 14.6591 | W | MAX
-0.03135 | 1.7721 | 340 | [15 empty] | Rajoitus | 14.6591 | W | 168
6V | [17 empty] | Tulopuhallin | 15.9533
2. aste polynomi | [11 empty] | Tarkistus, jos ei mittausalueella | [5 empty] | Elektroniikka | 4.4
A | B | C | [9 empty] | Paine yli | 350 | Pa
-0.025105 | 0.62918 | 203.1282 | [9 empty] | Alfa yli | 0.32 |  |  |  |  | Total power | 35.0124 | W
4V | [11 empty] | TRUE | [5 empty] | Maks qV | 26.9444 | l/s
2. aste polynomi | [17 empty] | SFP | 1.2994 | kW/m3/s
A | B | C | [9 empty] | 80 | 382.2937
-0.022467 | 0.0032873 | 94.9252 | [9 empty] | 90 | 354.5308
[12 empty] | 135 | 131.9295
9V lisämittaus
-0.039462 | 3.9323 | 320.2703 | [14 empty] | Verkkokäyrän potenssikäyrän termi
poistopuolen tilavuusviratmittaukset excelistä | [16 empty] | alfa
0.13774
[17 empty] | Verkkokäyrä mitoituspisteelle | [22 empty] | Tehostusvara
[17 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Järjestys muutettu
[17 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  | V | l/s |  |  |  |  | Maksimi tehostusvara |  | Tarkistus onko käyttöalueella
[17 empty] | 10 | -0.06582 | 8.4394 | 232.9787 | -0.20356 | -18.9471 | 60.4058 | 149.372 | 60.4058 | 502.5955 | 118.1345 | 64.3135 | 79.8521 |  | 10 | 60.4058 |  | 10 | 60.4058 |  |  |  |  | 124.2% |  | TRUE | (OK, jos TOSI)
[17 empty] | 8 | -0.03135 | 1.7721 | 340 | -0.16909 | -39.9065 | 50.3867 | 133.1733 | 50.3867 | 349.6983 | 68.6483 | 62.6189 | 75.9057 |  | 8 | 50.3867 |  | 9 | 55.0326 |  | 9 | 55.7813 | l/s | Haluttu tehostuspiste |  | Tehostuspisteen ohjausjännite
[17 empty] | 6 | -0.025105 | 0.62918 | 203.1282 | -0.16285 | -33.439 | 37.3027 | 99.9991 | 37.3027 | 191.6649 | 31.7412 | 55.7096 | 65.8484 |  | 6 | 37.3027 |  | 8 | 50.3867 |  |  |  |  | 29.6389 | l/s | 4.8024 | V
[17 empty] | 4 | -0.022467 | 0.0032873 | 94.9252 | -0.16021 | -24.3314 | 24.3519 | 61.5554 | 24.3519 | 81.6822 | 12.7085 | 42.1812 | 56.3206 |  | 4 | 24.3519 |  | 6 | 37.3027 |  |  |  |  | 121 | Pa
[17 empty] | 9 | -0.039462 | 3.9323 | 320.2703 | -0.1772 | -32.8418 | 55.0326 | 120 | 55.0326 | 417.1583 | 96.8542 |  |  |  | 9 | 55.0326 |  | 4 | 24.3519
[17 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[19 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[17 empty] | Poistokanava |  | 11 | 9 | 2 | -3 | -6 | -13 | -24 | -32 | ---> | 56.8514 | 54.8514 | 47.8514 | 42.8514 | 39.8514 | 32.8514 | 21.8514 | 13.8514 | 59.4544 | 45.88 | OK
[17 empty] | Jätekanava |  | 9 | 7 | 3 | -3 | -7 | -9 | -16 | -26 | ----> | 67.4915 | 65.4915 | 61.4915 | 55.4915 | 51.4915 | 49.4915 | 42.4915 | 32.4915 | 70.4793 | 58.73 | OK
[28 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[20 empty] | A | B | C
[19 empty] | 10V | -0.0030275 | 1.3879 | 45.3422
[19 empty] | 8V | -0.00069375 | 0.77076 | 31.5734
[19 empty] | 6V | 0.00076069 | 0.31459 | 18.9477
[19 empty] | 4V | 0.00085683 | 0.11014 | 9.5183
[19 empty] | 9V | 0.00099771 | 0.7768 | 51.0835
Mitatut pisteet
Poistokanava |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | Sovitteet 2. aste polynomi | [5 empty] | l/s | LwA | P |  | Sovitteet 2. aste polynomi | [5 empty] | l/s | W
10V | 142.3369 | 63.5048 | 168.3379 | A | B |  |  |  | 10V | 142.3109 | 76.3807 | 167.8298 |  | A | B | C |  |  | 10V | 145.9328 | 171.3366
| 135.5535 | 63.294 | 167.9612 | -9.1851e-05 | 0.007258 | 64.2102 |  |  |  | 135.753 | 75.6061 | 167.7629 |  | 0.0015813 | -0.36419 | 96.0815 |  |  |  | 141.0538 | 171.2048
| 120.8729 | 63.8585 | 167.8259 | [6 empty] | 121.885 | 75.2751 | 167.4385 | [7 empty] | 137.1494 | 170.5332
| 99.3543 | 64.0018 | 159.1945 | [6 empty] | 98.8459 | 75.5168 | 158.8284 | [7 empty] | 131.5549 | 170.8042
[20 empty] | 126.4531 | 170.4034
8V | 124.3962 | 60.7554 | 113.6032 | A | B |  |  |  | 8V | 124.3965 | 73.2742 | 113.3026 |  | A | B | C |  |  |  | 121.4682 | 169.7578
| 115.2858 | 59.8639 | 105.5586 | 0.0016134 | -0.30791 | 74.0374 |  |  |  | 115.28 | 72.0495 | 105.2986 |  | 0.002589 | -0.48814 | 93.9285 |  |  |  | 113.9745 | 167.399
| 101.6005 | 59.5003 | 97.9763 | [6 empty] | 101.9162 | 71.0791 | 97.7659 | [7 empty] | 98.8942 | 151.9457
| 86.8875 | 59.4372 | 86.9586 | [6 empty] | 83.8123 | 71.2005 | 86.7529 | [7 empty] | 82.5999 | 138.1508
[20 empty] | 59.6288 | 117.91
6V | 93.5096 | 54.4155 | 51.9634 | A | B | C |  |  | 6V | 93.746 | 66.5747 | 51.8407 |  | A | B | C |  |  |  | l/s | W
| 84.6032 | 53.4665 | 49.173 | 0.002663 | -0.37155 | 65.8638 |  |  |  | 83.8857 | 65.9002 | 49.0639 |  | 0.0019062 | -0.23534 | 71.9747 |  |  | 8V | 48.1138 | 66.9894
| 73.6372 | 52.9655 | 44.5872 | [6 empty] | 73.5289 | 64.7452 | 44.5202 | [7 empty] | 69.726 | 81.6244
| 62.441 | 53.0399 | 37.9588 | [6 empty] | 61.6046 | 64.7786 | 37.8969 | [7 empty] | 94.1458 | 99.9995
[20 empty] | 104.2146 | 103.4881
4V | 58.4401 | 45.0273 | 18.2887 | A | B | C |  |  | 4V | 58.4195 | 57.0409 | 18.2233 |  | A | B | C |  |  |  | 112.5722 | 108.2675
| 52.756 | 45.3909 | 17.1734 | -0.0038664 | 0.40538 | 34.6023 |  |  |  | 52.1969 | 56.4966 | 17.137 |  | 0.0031592 | -0.23928 | 60.2741 |  |  |  | 121.0832 | 114.1964
| 46.3831 | 44.9402 | 15.9765 | [6 empty] | 45.8921 | 55.8517 | 15.9708 | [7 empty] | 128.2598 | 120.0773
| 39.3321 | 44.6092 | 14.2864 | [6 empty] | 38.2254 | 55.7703 | 14.2532 | [7 empty] | l/s | W
[19 empty] | 6V | 95.2886 | 55.9264
[20 empty] | 84.2362 | 50.5993
[20 empty] | 67.2846 | 43.7967
[20 empty] | 38.7815 | 32.1103
[20 empty] | 28.1999 | 28.518
[20 empty] | l/s | W
[19 empty] | 4V | 18.2297 | 11.8293
[20 empty] | 38.3566 | 14.9067
[20 empty] | 50.652 | 17.4473
[20 empty] | 58.7134 | 18.8653
[20 empty] | l/s | W
[19 empty] | 9V | 120.1242 | 158.7186
[20 empty] | 104.2824 | 143.4085
[20 empty] | 70.6906 | 111.6079
[20 empty] | 49.5643 | 91.8764
[20 empty] | 88.6389 | 126.9145

## Laskenta vaipan läpi 130 (hidden)
Ohjausjännite
Tulo | 4.602 | V
Poisto | 4.3697 | V
Sovite ohj. Jännite vs. LwA vaipan läpi | [8 empty] | Mittausdataa
y = LwA, x = ohjausjännite | [8 empty] | Vohj | LwA
y = A*ln(x) + B | [8 empty] | 10 | 50.7278
[9 empty] | 10 | 50.9068
| A | B | [6 empty] | 10 | 51.6337
4 V - 10 V | 21.3783 | 1.9515 | [6 empty] | 8 | 46.8556
[9 empty] | 6 | 40.0817
[9 empty] | 4 | 31.5761
Maksimi | 4.602 | V | ---> | 34.5854 | dB
Painotettu keskiarvo | 4.5246 | V | ---> | 34.2227 | dB
Korjaus
Äänitehotasot kanaviin | [8 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lw | LwA
Imupuoli | Ulko | 45.3929 | dB |  |  |  |  | 10 V | 60.4746 | 60.9471 | 56.106 | 46.762 | 37.3678 | 30.6631 | 28.3877 | 22.1739 | 64.5056 | 50.7278
| Poisto | 46.4915 | dB |  |  |  |  | 8 V | 58.0925 | 57.9116 | 51.7639 | 42.078 | 33.3195 | 27.6711 | 24.8727 | 16.8024 | 61.5598 | 46.8556
| Erotus | 1.0986 | dB |  |  |  |  | 6 V | 52.8173 | 51.7556 | 44.3847 | 35.691 | 27.7342 | 21.673 | 17.5771 | 7.529 | 55.718 | 40.0817
[8 empty] | 4 V | 45.0155 | 42.2291 | 35.5693 | 29.0298 | 20.3674 | 11.962 | 5.3019 | 3.6171 | 47.241 | 31.5761
Painepuoli | Tulo | 60.2158 | dB
| Jäte | 60.7853 | dB | [5 empty] | 9.7468 | 10.2193 | 5.3782 | -3.9658 | -13.36 | -20.0647 | -22.3401 | -28.5539
| Erotus | 0.56953 | dB | [5 empty] | 11.2369 | 11.0561 | 4.9083 | -4.7775 | -13.536 | -19.1845 | -21.9828 | -30.0531
[9 empty] | 12.7356 | 11.6738 | 4.303 | -4.3907 | -12.3476 | -18.4088 | -22.5047 | -32.5527
Keskiarvo erotus | 0.83409 | dB | [6 empty] | 13.4394 | 10.6529 | 3.9932 | -2.5463 | -11.2088 | -19.6141 | -26.2742 | -27.959
Korjaus K | 4.5761 | dB | [5 empty] | KA | 11.7897 | 10.9005 | 4.6457 | -3.9201 | -12.6131 | -19.318 | -23.2754 | -29.7797 |  | tarkistus
[8 empty] | KA pyör | 12 | 11 | 5 | -4 | -13 | -19 | -23 | -30 |  | 0.20324 | OK
Taustamelukorjattu | 39.1614 | dB
Maksimikorjaus | 31.9854 | dB
|  |  |  | LpA10m2 | LpA2,5m2
Valinta | 34.2227 | dB |  | 30.2432 | 36.2638
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 12 | 11 | 5 | -4 | -13 | -19 | -23 | -30 | ---> | 46.2227 | 45.2227 | 39.2227 | 30.2227 | 21.2227 | 15.2227 | 11.2227 | 4.2227 | 49.2833 | 34.4259 | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta tulopuoli 60 (hidden)
Tuloilma tilavuusvirta vs. painehäviö | [5 empty] | Syötä piste
[6 empty] | 25 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [11 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 7,5 V |  | 5 V |  | 3 V
x = til.virta | [11 empty] | 18.1104 | -7.7146 | Ulko |  |  | ----> | Ulko | 50.5805 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 19.4742 | -0.6899 | Tulo |  |  | ----> | Tulo | 61.9951 | dB |  |  | 25 | 109.7222 | 20 | 96.508 | 12 | 59.0976 | 10 | 24.8561
2. aste polynomi | [22 empty] | 120 | 96.0497 | 100 | 83.3324 | 40 | 51.0413 | 20 | 20.1455
A | B | C | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 84.9809 | 150 | 74.1711 | 60 | 44.8522 | 30 | 15.2517
-0.025228 | -1.7571 | 521.5105 | [9 empty] | 3-7,5V | 6.2771 | -4.7635 |  |  | ---> | Tulopuhallin | 4.7416 | V | OK |  | 250 | 74.6059 | 200 | 64.0227 | 80 | 38.2116 | 35 | 12.729
[12 empty] | 7,5V - 10V | 2.4518 | 24.012 |  |  |  |  | TRUE |  |  |  | 320 | 61.0937 | 250 | 52.4767 | 100 | 31.0031 | 40 | 10.1515
7,5V | [17 empty] | Minimi-ilmavirta | 18 | l/s | Pulkkasen maili 14.6.19 |  | 390 | 45.3354 | 300 | 38.7213 | 125 | 20.9155
2. aste polynomi | [11 empty] | Polynomisovite teholle | [10 empty] | 410 | 40.2277 | 315 | 33.9211
A | B | C | [9 empty] | 0.054729 | -1.3285 | 14.2541 |  |  | ----> | Tulopuhallin | 15.2462 | W
-0.027491 | -1.1278 | 384.8881 | [15 empty] | Rajoitus | 15.2462 | W
5V | [17 empty] | Poistopuhallin | 15.2242
2. aste polynomi | [17 empty] | Elektroniikka | 3
A | B | C
-0.017129 | -1.589 | 165.727 | [15 empty] | Total power | 33.4705 | W
3V | [17 empty] | Maks qV | 26.9444 | l/s
2. aste polynomi | [17 empty] | SFP | 1.2422 | kW/m3/s
A | B | C
-0.008274 | -1.7505 | 58.6232
Verkkokäyrän potenssikäyrän termi
alfa
0.16
[17 empty] | Verkkokäyrä mitoituspisteelle | [13 empty] | Tehostusvara
[17 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA
[17 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella
[17 empty] | 10 | -0.025228 | -1.7571 | 521.5105 | -0.18523 | -58.0162 | 48.5298 | 109.7222 | 48.5298 | 376.8225 | 79.2029 | 62.5919 | 75.1907 |  | 94.12% |  |  | TRUE | (OK, jos TOSI)
[17 empty] | 7.5 | -0.027491 | -1.1278 | 384.8881 | -0.18749 | -48.4154 | 42.4003 | 96.508 | 42.4003 | 287.6462 | 55.4254 | 60.3368 | 72.754 |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[17 empty] | 5 | -0.017129 | -1.589 | 165.727 | -0.17713 | -35.4005 | 26.4298 | 59.0976 | 26.4298 | 111.7659 | 17.9393 | 51.2582 | 61.6999 |  | 27.5 | l/s |  | 5.1399 | V
[17 empty] | 3 | -0.008274 | -1.7505 | 58.6232 | -0.16827 | -24.5776 | 14.1747 | 24.8561 | 14.1747 | 32.1475 | 6.2119 | 40.4464 | 51.574 |  | 121 | Pa
[17 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[19 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[17 empty] | Ulkokanava |  | 23 | 6 | 3 | -6 | -16 | -22 | -30 | -33 | ---> | 73.5805 | 56.5805 | 53.5805 | 44.5805 | 34.5805 | 28.5805 | 20.5805 | 17.5805 | 73.7147 | 50.6112 | OK
[17 empty] | Tulokanava |  | 21 | 4 | 0 | -3 | -9 | -11 | -16 | -24 | ----> | 82.9951 | 65.9951 | 61.9951 | 58.9951 | 52.9951 | 50.9951 | 45.9951 | 37.9951 | 83.1392 | 62.0249 | OK
[28 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[20 empty] | A | B | C
[19 empty] | 10V | -0.0020231 | 0.98156 | 36.3329
[19 empty] | 7,5V | -0.003446 | 1.0152 | 18.5762
[19 empty] | 5V | 0.0010599 | 0.20073 | 11.8937
[19 empty] | 3V | 0.0019762 | 0.0060953 | 5.7285
Mitatut pisteet
Ulkokanava |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P |  | 3. aste polynomisovitus | [5 empty] | l/s | W
10V | 96.7236 | 60.5991 | 113.2795 | A | B |  |  |  | 10V | 100.8083 | 73.4631 | 113.6544 |  | A | B | C |  |  | 10V | 96.7236 | 113.2795
| 80.3545 | 61.3627 | 102.8744 | -0.040952 | 64.5793 |  |  |  |  | 84.3627 | 72.8443 | 104.8704 |  | 0.0020059 | -0.3325 | 86.6026 |  |  |  | 80.3545 | 102.8744
| 63.4464 | 61.8966 | 83.3497 | [6 empty] | 66.0191 | 73.3775 | 91.7269 | [7 empty] | 42.5873 | 75.2455
| 42.5873 | 62.8647 | 75.2455 | [6 empty] | 50.8855 | 74.8836 | 80.1236 | [7 empty] | 100.8083 | 113.6544
[20 empty] | 84.3627 | 104.8704
7,5 V | 82.9973 | 59.138 | 78.256 | A | B |  |  |  | 7,5 V | 89.2614 | 70.8979 | 81.8103 |  | A | B | C |  |  |  | 66.0191 | 91.7269
| 70.8973 | 59.3179 | 72.8026 | -0.033241 | 61.7462 |  |  |  |  | 74.5991 | 70.7101 | 76.6279 |  | 0.0022925 | -0.3395 | 83.0275 |  |  |  | 50.8855 | 80.1236
| 54.9809 | 59.6641 | 56.4672 | [6 empty] | 57.1855 | 70.8309 | 65.4075 | [7 empty] | l/s | W
| 37.3827 | 60.6788 | 52.379 | [6 empty] | 45.0109 | 72.5099 | 56.2731 | [6 empty] | 7,5V | 82.9973 | 78.256
[20 empty] | 70.8973 | 72.8026
5V | 52.3109 | 50.9453 | 25.3258 | A | B | C |  |  | 5V | 54.8 | 61.4259 | 25.9528 |  | A | B | C |  |  |  | 37.3827 | 52.379
| 45.1909 | 50.9312 | 22.776 | -0.0010142 | 0.064609 | 50.2591 |  |  |  | 46.8564 | 61.4251 | 24.1438 |  | -0.0010849 | 0.075669 | 60.4579 |  |  |  | 89.2614 | 81.8103
| 33.94 | 51.4224 | 18.1657 | [6 empty] | 36.4927 | 61.952 | 20.5006 | [7 empty] | 74.5991 | 76.6279
| 23.01 | 51.1646 | 17.0676 | [6 empty] | 26.9345 | 61.6482 | 18.1327 | [7 empty] | 57.1855 | 65.4075
[20 empty] | 45.0109 | 56.2731
3V | 26.1609 | 39.9506 | 7.1297 | A | B | C |  |  | 3V | 26.4279 | 50.527 | 7.2464 |  | A | B | C |  |  |  | l/s | W
| 23.1227 | 40.8912 | 7.1955 | -0.027752 | 1.0798 | 30.716 |  |  |  | 23.4164 | 50.6804 | 6.9733 |  | -0.0057282 | 0.13957 | 50.7466 |  |  | 5V | 52.3109 | 25.3258
| 18.2882 | 41.1522 | 6.0547 | [6 empty] | 18.35 | 51.5282 | 6.7233 | [7 empty] | 45.1909 | 22.776
| 11.8782 | 39.6341 | 6.0736 | [6 empty] | 13.6236 | 51.5361 | 6.2531 | [7 empty] | 23.01 | 17.0676
[20 empty] | 54.8 | 25.9528
[20 empty] | 46.8564 | 24.1438
[20 empty] | 36.4927 | 20.5006
[20 empty] | 26.9345 | 18.1327
[20 empty] | l/s | W
[19 empty] | 3V | 26.1609 | 7.1297
[20 empty] | 23.1227 | 7.1955
[20 empty] | 18.2882 | 6.0547
[20 empty] | 26.4279 | 7.2464
[20 empty] | 23.4164 | 6.9733
[20 empty] | 18.35 | 6.7233
[20 empty] | 13.6236 | 6.2531

## Laskenta poistopuoli 60 (hidden)
Poistoilma tilavuusvirta vs. painehäviö | [5 empty] | Syötä piste
[6 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [11 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 7,5 V |  | 5 V |  | 3 V
x = til.virta | [11 empty] | 20.1883 | -15.8415 | Poisto |  |  | ----> | Poisto | 50.6542 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 20.2489 | -5.8586 | Jäte |  |  | ----> | Jäte | 60.8369 | dB |  |  | 25 | 116.5344 | 24 | 112.687 | 17 | 72.2846 | 10 | 36.1004
2. aste polynomi | [22 empty] | 120 | 106.0429 | 100 | 101.1625 | 40 | 65.0385 | 20 | 30.2289
A | B | C | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 97.2291 | 150 | 92.6182 | 60 | 58.1733 | 30 | 23.2117
-0.057649 | 3.7763 | 367.8147 | [9 empty] | 3-7,5V | 7.0935 | -5.0219 |  |  | ---> | Poistopuhallin | 4.5065 | V |  |  | 250 | 88.5776 | 200 | 82.9624 | 80 | 50.6163 | 35 | 18.9831
[12 empty] | 7,5V - 10V | 2.2923 | 31.1908 |  |  |  |  | TRUE |  |  |  | 320 | 76.3666 | 250 | 71.5994 | 100 | 42.1036 | 43 | 10.0866
7,5V | [17 empty] | Minimi qV | 18 | l/s | Pulkkasen maili 14.6.19 |  | 390 | 58.9808 | 300 | 57.0731 | 140 | 19.5749
2. aste polynomi | [11 empty] | Polynomisovite teholle | [10 empty] | 422 | 44.2778 | 340 | 39.2543
A | B | C | [9 empty] | 0.04633 | -1.1762 | 13.2812 |  |  | ----> | Poistopuhallin | 15.2242 | W
-0.037013 | 1.3205 | 345.1969 | [15 empty] | Rajoitus | 15.2242 | W
5V
2. aste polynomi
A | B | C
-0.018489 | -0.63512 | 159.5171
3V
2. aste polynomi
A | B | C
-0.021576 | -0.27202 | 47.9389
Verkkokäyrän potenssikäyrän termi
alfa
0.13774
[17 empty] | Verkkokäyrä mitoituspisteelle | [13 empty] | Tehostusvara
[17 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA
[17 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Poisto | Jäte |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella
[17 empty] | 10 | -0.057649 | 3.7763 | 367.8147 | -0.19539 | -34.787 | 54.1142 | 116.5344 | 54.1142 | 403.3515 | 85.2595 | 64.8815 | 74.8016 |  | 100.8% |  |  | TRUE | (OK, jos TOSI)
[17 empty] | 7.5 | -0.037013 | 1.3205 | 345.1969 | -0.17475 | -40.8268 | 48.3833 | 112.687 | 48.3833 | 322.4431 | 64.8927 | 61.8469 | 72.9346 |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[17 empty] | 5 | -0.018489 | -0.63512 | 159.5171 | -0.15623 | -34.051 | 29.9857 | 72.2846 | 29.9857 | 123.8481 | 19.6322 | 53.6418 | 62.8709 |  | 29.6389 | l/s |  | 4.8863 | V
[17 empty] | 3 | -0.021576 | -0.27202 | 47.9389 | -0.15932 | -18.2213 | 16.5139 | 36.1004 | 16.5139 | 37.5628 | 6.5052 | 40.4173 | 50.9659 |  | 121 | Pa
[17 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[19 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[17 empty] | Poistokanava |  | 23 | 4 | -1 | -4 | -10 | -17 | -26 | -32 | ---> | 73.6542 | 54.6542 | 49.6542 | 46.6542 | 40.6542 | 33.6542 | 24.6542 | 18.6542 | 73.7367 | 50.5239 | OK
[17 empty] | Jätekanava |  | 20 | 4 | 2 | -5 | -8 | -10 | -15 | -19 | ----> | 80.8369 | 64.8369 | 62.8369 | 55.8369 | 52.8369 | 50.8369 | 45.8369 | 41.8369 | 81.037 | 60.8869 | OK
[28 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[20 empty] | A | B | C
[19 empty] | 10V | -0.013544 | 2.7452 | -23.6319
[19 empty] | 7,5V | 0.0002376 | 0.64971 | 32.9015
[19 empty] | 5V | -0.0013806 | 0.47197 | 6.7211
[19 empty] | 3V | 0.0025923 | -0.018306 | 6.1005
Mitatut pisteet
Poistokanava |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P |  | 3. aste polynomisovitus | [5 empty] | l/s | W
10V | 107.8747 | 63.4939 | 115.5265 | A | B |  |  |  | 10V | 105.8799 | 74.1531 | 114.5115 |  | A | B | C |  |  | 10V | 107.8747 | 115.5265
| 100.3894 | 63.298 | 115.6155 | -0.028461 | 66.4216 |  |  |  |  | 93.8742 | 74.0197 | 114.5915 |  | 0.00016443 | -0.040117 | 76.491 |  |  |  | 100.3894 | 115.6155
| 81.4487 | 64.2727 | 105.5312 | [6 empty] | 78.1995 | 74.4738 | 107.9749 | [7 empty] | 53.0899 | 82.4673
| 53.0899 | 64.8654 | 82.4673 | [6 empty] | 56.0825 | 74.7319 | 89.4535 | [7 empty] | 105.8799 | 114.5115
[20 empty] | 93.8742 | 114.5915
7,5 V | 101.3108 | 61.7936 | 98.8841 | A | B |  |  |  | 7,5 V | 102.3583 | 73.4984 | 105.1358 |  | A | B | C |  |  |  | 78.1995 | 107.9749
| 91.9425 | 61.6992 | 90.8407 | -0.0033953 | 62.0112 |  |  |  |  | 86.9619 | 72.3467 | 94.4427 |  | 0.00092351 | -0.13111 | 77.1165 |  |  |  | 56.0825 | 89.4535
| 73.0663 | 61.4995 | 77.4087 | [6 empty] | 71.1664 | 72.7601 | 84.0267 | [7 empty] | l/s | W
| 47.0354 | 61.9887 | 60.5961 | [6 empty] | 48.9919 | 72.8373 | 68.838 | [6 empty] | 7,5V | 101.3108 | 98.8841
[20 empty] | 91.9425 | 90.8407
5V | 65.4528 | 52.8683 | 31.2127 | A | B | C |  |  | 5V | 64.7159 | 63.9764 | 31.9554 |  | A | B | C |  |  |  | 73.0663 | 77.4087
| 57.9937 | 52.7121 | 28.4597 | 0.0012183 | -0.13873 | 56.7063 |  |  |  | 56.3976 | 63.6997 | 30.2388 |  | 0.00068253 | -0.031472 | 63.201 |  |  |  | 47.0354 | 60.5961
| 44.9342 | 52.9631 | 23.5903 | [6 empty] | 44.3647 | 63.0715 | 24.5431 | [7 empty] | 102.3583 | 105.1358
| 29.3784 | 53.6741 | 18.7143 | [6 empty] | 29.7093 | 62.8884 | 20.3173 | [7 empty] | 86.9619 | 94.4427
[20 empty] | 71.1664 | 84.0267
3V | 34.8168 | 42.3663 | 8.5753 | A | B | C |  |  | 3V | 35.2384 | 51.5187 | 8.7615 |  | A | B | C |  |  |  | 48.9919 | 68.838
| 30.15 | 42.1073 | 7.49 | -0.0039837 | 0.3107 | 36.3727 |  |  |  | 30.2249 | 51.2871 | 8.1737 |  | -0.0026013 | 0.1598 | 49.0363 |  |  |  | l/s | W
| 24.397 | 41.591 | 6.8879 | [6 empty] | 24.5174 | 51.5413 | 7.6408 | [6 empty] | 5V | 65.4528 | 31.2127
| 16.4603 | 40.4055 | 6.109 | [6 empty] | 14.8404 | 50.8055 | 6.3783 | [7 empty] | 57.9937 | 28.4597
[20 empty] | 29.3784 | 18.7143
[20 empty] | 64.7159 | 31.9554
[20 empty] | 56.3976 | 30.2388
[20 empty] | 44.3647 | 24.5431
[20 empty] | 29.7093 | 20.3173
[20 empty] | l/s | W
[19 empty] | 3V | 34.8168 | 8.5753
[20 empty] | 30.15 | 7.49
[20 empty] | 24.397 | 6.8879
[20 empty] | 35.2384 | 8.7615
[20 empty] | 30.2249 | 8.1737
[20 empty] | 24.5174 | 7.6408
[20 empty] | 14.8404 | 6.3783

## Laskenta keittiöohitus (hidden)
Poistopuolen mitoituspiste
qV | 26.9444 | dm3/s
Pd | 100 | Pa
Vohj | 4.3915 | V
100 Pa Verkkokäyrän LwA vs. Vohj sovite
3V - 7,5 V ohjausalue | A | B
Logaritmisovite LwA = A*ln(Vohj) + B | 22.9447 | 22.0111 | --> | 55.9618 | dB
7,5V - 10V ohjausalue | A | B
Lineaarisovite LwA = A*Vohj + B | 0.9772 | 60.9698 | --> | 65.2612 | dB
Valinta logaritmi vs. lineaarisovite | LwA | 55.9618 | dB
Raja-arvot
Verkkokäyräkorjaus kokonaistasoon | [5 empty] | Verkkokäyrä |  | 140 Pa | 100 Pa | 50 Pa
Verkkokäyrän alfatermi | 0.13774 |  |  |  |  | Verkkokäyrän alfa |  | 0.302 | 0.051 | 0.0131
Neliöjuuri alfa | 0.37113 |  |  |  |  | Neliöjuuri alfa |  | 0.54955 | 0.22583 | 0.11446
[6 empty] | dB korjaus |  | -2.4 | 0 | 1
| A | B
Lineaarisovite korjaukselle | -7.7247 | 1.8245 | --> | -1.0423 | dB
Korjattu kokonaistaso | LwA | 54.9195 | dB
Spektri | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lw | LwA tark.
Korjaustermi | 13 | 8 | 4 | -3 | -6 | -15 | -26 | -34
Mitoituspisteen spektri 100 Pa verkkokäyrällä | 68 | 63 | 59 | 52 | 49 | 40 | 29 | 21 | 69.7072 | 55.3571
a-painotus | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta vaipan läpi 60 (hidden)
Ohjausjännite
Tulo | 4.7416 | V
Poisto | 4.5065 | V
Sovite ohj. Jännite vs. LwA vaipan läpi
y = LwA, x = ohjausjännite
y = Ax + B
| A | B
7,5 V - 10 V | 6.5052 | 34.2837
4 V - 7,5 V | 24.7442 | -2.5013
Maksimi | 4.7416 | V | ---> | 36.0099 | dB
Painotettu keskiarvo | 4.6632 | V | ---> | 35.5975 | dB
Korjaus
Äänitehotasot kanaviin
Imupuoli | Ulko | 45.3929 | dB
| Poisto | 46.4915 | dB
| Erotus | 1.0986 | dB
Painepuoli | Tulo | 60.2158 | dB
| Jäte | 60.7853 | dB
| Erotus | 0.56953 | dB
Keskiarvo erotus | 0.83409 | dB
Korjaus K | 4.5761 | dB
Taustamelukorjattu | 40.586 | dB
Maksimikorjaus | 33.4099 | dB
|  |  |  | LpA10m2 | LpA2,5m2
Valinta | 35.5975 | dB |  | 31.6181 | 37.6387
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 14 | 10 | 5 | -4 | -12 | -18 | -25 | -26 | ---> | 49.5975 | 45.5975 | 40.5975 | 31.5975 | 23.5975 | 17.5975 | 10.5975 | 9.5975 | 51.4818 | 35.695 | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta tulopuoli 250 (hidden)
[14 empty] | Paine puhaltimen yli (2. aste polyn) | [9 empty] | 7,5 V | -0.0062567 | 0.52719 | 353.8343
| Tuloilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste | [5 empty] | 0.092871 | 3.9263 | -38.9824 |  |  |  | Paine puh. yli | 117.2201 | Pa | [22 empty] | ILMAN PATTERIA
[8 empty] | 25 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten | [11 empty] | SFPINT -LASKENTA | [7 empty] | 10V | -0.0063124 | 0.63458 | 646.4254
| y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 7,5 V |  | 7,5 V |  | 6 V |  | 4 V | [13 empty] | 8V | -0.0058938 | 0.41705 | 424.6537
| x = til.virta | [12 empty] | 20.0151 | -25.3199 | Ulko |  |  | ----> | Ulko | 39.1062 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  |  |  |  | Suodatinkorjaus | 0 | [6 empty] | 6V | -0.006901 | 0.58828 | 199.2324
| 10V | [12 empty] | 18.6102 | -3.6234 | Tulo |  |  | ----> | Tulo | 56.2805 | dB |  |  | 20 | 276.93 | 20 | 276.93 | 10 | 213.6134 | 10 | 122.8515 |  |  |  |  | Tuloilman lämpötilahyötysuhde | 79.5% | [6 empty] | 4V | -0.0045287 | -0.1767 | 100.0578
| 2. aste polynomi | [23 empty] | 50 | 266.4873 | 50 | 266.4873 | 50 | 195.729 | 20 | 114.8725 | [12 empty] | PATTERIN KANSSA
| A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos | [6 empty] | 100 | 247.9086 | 100 | 247.9086 | 90 | 175.4582 | 40 | 97.2905 |  |  |  |  | Tulopuhaltimen paine-ero | 117.2201 | Pa | [5 empty] | 10V | -0.0063692 | 0.61219 | 647.1064
| -0.0063124 | 0.63458 | 646.4254 | [10 empty] | 3-9V | 6.9344 | -4.1549 |  | 4.2044 | ---> | Tulopuhallin | 4.1973 | V | OK |  | 150 | 227.4767 | 150 | 227.4767 | 130 | 151.4758 | 60 | 76.5423 |  |  |  |  | Poistopuhaltimen paine-ero | 108.0444 | Pa | [5 empty] | 8V | -0.0059568 | 0.39696 | 425.1453
[14 empty] | 9V - 10V | 6.0269 | 4.0128 |  | 3.4823 |  |  | FALSE |  |  |  | 230 | 188.9877 | 230 | 188.9877 | 170 | 120.4219 | 80 | 49.8423 | [12 empty] | 6V | -0.0069707 | 0.56997 | 199.6307
| 8V | [12 empty] | Kaikki 2. x = l/s, y = Vohj | -3.6479e-05 | 0.15 | 0.45584 | 4.183 |  | Minimi qV | 40 | l/s |  |  | 300 | 144.0084 | 300 | 144.0084 | 205 | 73.943 | [6 empty] | Tulopuhaltimen hyötysuhde | 12.31% | [6 empty] | 4V | -0.0046179 | -0.19088 | 100.2451
| 2. aste polynomi | [12 empty] | Polynomisovite teholle | [10 empty] | 340 | 105.2654 | 340 | 105.2654 | [8 empty] | Poistopuhaltimen hyötysuhde | 13.08%
| A | B | C | [9 empty] | 2.aste | 0.082273 | -3.1231 | 50.5324 |  |  | ----> | Tulopuhallin | 23.8021 | W | max | [21 empty] | Onko patteri?
| -0.0058938 | 0.41705 | 424.6537 | [9 empty] | 3.aste | 0.00070062 | -0.010648 | 0.73353 | 1.0986 |  |  | Rajoitus | 23.8021 | W | 516 | W | [12 empty] | SFP_int_limit | 1291.25 | [6 empty] | FALSE
7.5 V | -0.0062567 | 0.52719 | 353.8343
| 6V | [11 empty] | 2.aste | 23.8749 | W |  |  |  |  | Poistopuhallin | 22.2623 | [15 empty] | SFP_int_tulo | 139.8647 | [6 empty] | Valinta
| 2. aste polynomi | [11 empty] | 3.aste | 23.7293 | W |  |  |  |  | Elektroniikka | 2.37 | [15 empty] | SFP_int_poisto | 61.5164 | [6 empty] | 10 V | -0.0063124 | 0.63458 | 646.4254
| A | B | C | [9 empty] | KA | 23.8021 | W | [21 empty] | SFP_int_KOK | 201.3811 | [6 empty] | 8 V | -0.0058938 | 0.41705 | 424.6537
| -0.006901 | 0.58828 | 199.2324 | [16 empty] | Total power | 48.4343 | W | [22 empty] | 6V | -0.006901 | 0.58828 | 199.2324
[45 empty] | 4V | -0.0045287 | -0.1767 | 100.0578
| 4V | [11 empty] | Validointipiste | [6 empty] | Maks qV | 26.9444 | l/s
| 2. aste polynomi | [11 empty] | 165 | l/s | [5 empty] | SFP | 1.7976 | kW/m3/s | [22 empty] | 7.5 V
| A | B | C | [9 empty] | 198 | Pa | [30 empty] | ILMAN PATTERIA | -0.0062567 | 0.52719 | 353.8343
| -0.0045287 | -0.1767 | 100.0578 | [41 empty] | PATTERIN KANSSA | -0.0063537 | 0.5188 | 353.3893
[19 empty] | Verkkokäyrän potenssikäyrän termi (y=ax^2 --> a = y/x^2) | [25 empty] | Valinta | -0.0062567 | 0.52719 | 353.8343
alfa
0.16
[19 empty] | Verkkokäyrä mitoituspisteelle | [20 empty] | Tehostusvara
[19 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Paine puhaltimen yli
[19 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s | [5 empty] | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella
[19 empty] | 10 | -0.0063124 | 0.63458 | 646.4254 | -0.16631 | -60.4657 | 64.2813 | 276.93 | 64.2813 | 661.1332 | 190.3508 | 58.687 | 73.7223 |  | 10 | 64.2813 |  | 599.4104 | Pa |  |  | 90.98% |  |  | TRUE | (OK, jos TOSI)
[19 empty] | 8 | -0.0058938 | 0.41705 | 424.6537 | -0.16589 | -49.353 | 51.867 | 276.93 | 51.867 | 430.4293 | 108.2599 | 52.2965 | 69.4975 |  | 9 | 58.2544 |  | 408.6327 | Pa |  |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[19 empty] | 6 | -0.006901 | 0.58828 | 199.2324 | -0.1669 | -32.8327 | 36.3575 | 213.6134 | 36.3575 | 211.4986 | 47.365 | 47.625 | 64.2504 |  | 8 | 51.867 |  | 232.4532 | Pa |  |  | 27.5 | l/s |  | 4.561 | V
[19 empty] | 4 | -0.0045287 | -0.1767 | 100.0578 | -0.16453 | -25.2035 | 24.1295 | 122.8515 | 24.1295 | 93.1572 | 22.4419 | 38.1124 | 55.1192 |  | 6 | 36.3575 |  | 107.5278 | Pa |  |  | 121 | Pa
[19 empty] | 7.5 | -0.0062567 | 0.52719 | 353.8343 | -0.16626 | -44.5746 | 47.7456 | 276.93 | 47.7456 | 364.7424 | Model 250 rajoitettu max 7,5 V |  |  |  | 4 | 24.1295 | [8 empty] | Tulos
[42 empty] | 3-9V | 4.5649 | V | T9
[19 empty] | Spektrikorjaukset |  | Lwokt = LwA + K | [20 empty] | 9V - 10V | 3.8971 | V | T10
[42 empty] | Kaikki 2. x = l/s, y = Vohj | 4.5532 | V | T11
[21 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[19 empty] | Ulkokanava |  | 15 | 13 | 1 | -5 | -9 | -14 | -24 | -29 | ---> | 54.1062 | 52.1062 | 40.1062 | 34.1062 | 30.1062 | 25.1062 | 15.1062 | 10.1062 | 56.3752 | 39.4208 | OK
[19 empty] | Tulokanava |  | 6 | 8 | -1 | -4 | -5 | -10 | -14 | -16 | ----> | 62.2805 | 64.2805 | 55.2805 | 52.2805 | 51.2805 | 46.2805 | 42.2805 | 40.2805 | 67.0593 | 56.2029 | OK
[30 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[22 empty] | A | B | C | [12 empty] | Tehon sovitteet 2. aste polynomi
[21 empty] | 10V | 0.00037769 | 0.95964 | 127.1033 | [13 empty] | A | B | C
[21 empty] | 6,5V | 0.00058205 | 0.59865 | 75.6441 | [12 empty] | 10V | -0.0078887 | 3.1314 | 430.7164
[21 empty] | 5V | 0.000119 | 0.44802 | 30.9188 | [12 empty] | 6,5V | -0.0067204 | 2.2461 | 310.2146
[21 empty] | 3V | 7.844e-05 | 0.19954 | 17.5814 | [12 empty] | 5V | -0.0055201 | 1.3814 | 189.5261
[37 empty] | 3V | -0.003047 | 0.51216 | 96.9437
Mitatut pisteet
| Ulkokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta | [15 empty] | Paine puhaltimen yli
|  | l/s | LwA | P |  | Sovitteet 2. ja 1. aste ja logaritmi | [5 empty] | l/s | LwA | P |  | Sovitteet 2. ja 1. aste ja logaritmi | [5 empty] | l/s | W | [13 empty] | Teho vs tilavuusvirta
| 10V | 344.7 | 62.1447 | 504.4911 |  | A | B |  | LwA lask. |  | 10V | 347.5588 | 81.8515 | 500.7667 |  | A | B | C | LwA lask |  | 10V | 149.9263 | 269.8713 | [14 empty] | l/s | Ps puh
|  | 324 | 61.1108 | 469.6243 | 2.aste | 0.0001316 | -0.06156 | 67.5623 | 64.1489 |  |  | 318.5737 | 81.0641 | 470.189 | 2.aste | 4.3666e-05 | -0.00025165 | 76.6781 | 76.8423 |  |  | 207.4229 | 344.2411 | [13 empty] | 10V | 149.9263 | 722.4261
|  | 292.5 | 60.9854 | 439.4751 | Lin. | 0.0090497 | 58.5587 |  | 59.1404 |  |  | 289.3128 | 80.2368 | 441.0612 | Lineaarinen | 0.023651 | 73.5392 |  | 75.0595 |  |  | 261.1074 | 404.7493 | [14 empty] | 207.4229 | 739.5303
|  | 199.8 | 60.5004 | 336.6081 | Log | 2.2906 | 48.2439 |  | 57.7803 |  |  | 207.4229 | 78.5071 | 345.3257 | Log | 6.2824 | 44.8927 |  | 71.0479 |  |  | 289.3128 | 441.2144 | [14 empty] | 261.1074 | 717.8806
[22 empty] | 320.5409 | 476.0109 | [14 empty] | 289.3128 | 675.419
| 8V | 281.5 | 58.2423 | 289.3769 |  | A | B |  |  |  | 8V | 283.9677 | 77.7354 | 293.3694 |  | A | B | C |  |  |  | 348.7793 | 508.6455 | [14 empty] | 320.5409 | 623.2369
|  | 263.3 | 57.7216 | 271.2288 | 2.aste | 6.9042e-05 | -0.0089937 | 55.303 | 55.0223 |  |  | 261.9698 | 76.8629 | 272.8589 | 2.aste | 8.8478e-05 | -0.010385 | 73.538 | 73.2373 |  |  | 318.5737 | 470.2501 | [14 empty] | 348.7793 | 572.2875
|  | 237.6 | 57.0637 | 247.399 | Lin. | 0.021305 | 52.1378 |  | 53.2428 |  |  | 234.5567 | 75.9863 | 250.0643 | Lineaarinen | 0.029049 | 69.3314 |  | 70.8381 |  |  | 347.5588 | 500.7054 | [14 empty] | 318.5737 | 618.0453
|  | 163.8 | 55.6823 | 188.5718 | Log | 4.5249 | 32.5365 |  | 50.4038 |  |  | 167.4512 | 74.2778 | 194.6131 | Log | 6.2654 | 42.0763 |  | 66.8163 |  |  | 88.3954 | 219.5172 | [14 empty] | 347.5588 | 562.7672
[38 empty] | 88.3954 | 748.2212
| 4V | 199.7 | 52.0546 | 128.6916 |  | A | B | C |  |  | 4V | 196.5959 | 70.2945 | 120.3465 |  | A | B | C |  |  |  | l/s | W
|  | 189.6 | 50.8778 | 112.5589 | 2.aste | 0.00065254 | -0.18352 | 62.5137 | 56.704 |  |  | 188.2497 | 70.3939 | 121.4732 | 2.aste | 6.1523e-05 | 0.012551 | 65.609 | 66.1466 |  | 8 V | 117.9562 | 149.6922 | [14 empty] | l/s | Ps puh
|  | 172.1 | 50.4007 | 106.1296 | Lin. | 0.01969 | 47.4936 |  | 48.2095 |  |  | 164.3849 | 69.2385 | 108.1734 | Lineaarinen | 0.031871 | 64.1536 |  | 65.3124 |  |  | 167.4512 | 194.213 | [13 empty] | 8 V | 117.9562 | 480.4774
|  | 116.3 | 49.9852 | 85.3268 | Log | 2.8809 | 36.1037 |  | 46.456 |  |  | 119.6571 | 68.0057 | 85.8109 | Log | 4.8784 | 44.5964 |  | 62.1264 |  |  | 209.8673 | 226.8631 | [14 empty] | 167.4512 | 499.2532
[22 empty] | 234.5567 | 250.0149 | [14 empty] | 209.8673 | 489.6027
| 2V | 120.9 | 42.7142 | 42.3082 |  | A | B | C |  |  | 2V | 120.0669 | 60.2774 | 42.2554 |  | A | B | C |  |  |  | 285.0541 | 291.7599 | [14 empty] | 234.5567 | 465.3622
|  | 111.7 | 41.5822 | 40.4953 | 2.aste | 0.0019023 | -0.33292 | 55.1219 | 48.1964 |  |  | 110.2138 | 59.7453 | 41.1737 |  | 0.00032825 | -0.017145 | 57.6158 | 57.3932 |  |  | 262.7163 | 272.3613 | [14 empty] | 285.0541 | 405.8321
|  | 102.2 | 41.0263 | 37.4605 | Lin. | 0.035781 | 37.8686 |  | 38.7319 |  |  | 101.5421 | 59.2375 | 38.9035 | Lineaarinen | 0.044751 | 54.8202 |  | 55.9 |  |  | 261.9698 | 272.8671 | [14 empty] | 262.7163 | 432.6514
|  | 75.4 | 40.8288 | 31.8561 | Log | 3.2581 | 26.5015 |  | 36.8733 |  |  | 71.5108 | 58.0702 | 32.2842 | Log | 4.0906 | 40.5355 |  | 53.5577 |  |  | 283.9677 | 293.3486 | [14 empty] | 261.9698 | 433.6376
[22 empty] | 69.7466 | 122.3434 | [14 empty] | 283.9677 | 410.0083
[22 empty] | l/s | W
[21 empty] | 6V | 81.2767 | 68.3381 | [14 empty] | l/s | Ps puh
[22 empty] | 119.6571 | 85.8179 | [13 empty] | 6V | 81.2767 | 265.005
[22 empty] | 150.5971 | 100.5821 | [14 empty] | 119.6571 | 275.7212
[22 empty] | 164.3849 | 108.185 | [14 empty] | 150.5971 | 277.9894
[22 empty] | 191.8027 | 122.0671 | [14 empty] | 164.3849 | 260.1718
[22 empty] | 202.1015 | 127.0358 | [14 empty] | 191.8027 | 256.3865
[22 empty] | 188.2497 | 121.4744 | [14 empty] | 202.1015 | 247.7545
[22 empty] | 196.5959 | 120.3453 | [14 empty] | 188.2497 | 256.2777
[38 empty] | 196.5959 | 237.9663
[22 empty] | l/s | W
[21 empty] | 4V | 49.9063 | 27.7891 | [14 empty] | l/s | Ps puh
[22 empty] | 71.5108 | 32.2847 | [13 empty] | ¤ V | 49.9063 | 115.4382
[22 empty] | 90.0432 | 35.6402 | [14 empty] | 71.5108 | 116.497
[22 empty] | 101.5421 | 38.9023 | [14 empty] | 90.0432 | 119.1784
[22 empty] | 119.0326 | 42.4215 | [14 empty] | 101.5421 | 118.075
[22 empty] | 110.2138 | 41.1739 | [14 empty] | 119.0326 | 114.8876
[22 empty] | 120.0669 | 42.2551 | [14 empty] | 110.2138 | 116.4471
[38 empty] | 120.0669 | 113.8894

## Laskenta poistopuoli 250 (hidden)
Paine puhaltimen yli (2. aste polyn)
| Poistoilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste | [5 empty] | 0.095392 | 2.4304 | -26.6976 |  |  |  | Paine puh. yli | 108.0444 | Pa
[8 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
| y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 7,5 V |  | 7,5 V |  | 6 V |  | 4 V |  |  | 7,5 V
| x = til.virta | [12 empty] | 18.5431 | -21.9163 | Poisto |  |  | ----> | Poisto | 39.1606 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  | -0.0053125 | 0.44481 | 359.5985
| 10V | [12 empty] | 21.1631 | -16.4004 | Jäte |  |  | ----> | Jäte | 53.3063 | dB |  |  | 25 | 296.297 | 25 | 296.297 | 10 | 231.4548 | 10 | 137.7948
| 2. aste polynomi | [23 empty] | 100 | 266.8495 | 100 | 266.8495 | 50 | 211.5621 | 20 | 129.5056
| A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos | [6 empty] | 200 | 220.1752 | 200 | 220.1752 | 90 | 189.1132 | 40 | 110.9257
| -0.006814 | 1.1894 | 585.3381 | [10 empty] | 3-9V | 7.6286 | -5.4129 |  | 4.2416 | ---> | Poistopuhallin | 4.2384 | V | OK |  | 230 | 203.5669 | 230 | 203.5669 | 130 | 162.7615 | 60 | 88.0985
[14 empty] | 9V - 10V | 4.6359 | 21.5217 |  | 1.1697 |  |  | FALSE |  |  |  | 270 | 178.3132 | 270 | 178.3132 | 170 | 129.2695 | 80 | 55.1025
| 8V | [12 empty] | Kaikki 2. x = l/s, y = Vohj | 0.00039243 | 0.10228 | 1.1912 | 4.232 |  | Minimi qV | 40 | l/s |  |  | 300 | 155.7556 | 300 | 155.7556 | 200 | 92.4087
| 2. aste polynomi | [12 empty] | Polynomisovite teholle | [10 empty] | 340 | 115.6328 | 340 | 115.6328
| A | B | C | [9 empty] | 2.aste | -0.011711 | 3.6163 | -65.9507 |  |  | ----> | Poistopuhallin | 22.2623 | W | max
| -0.0051982 | 0.42948 | 423.1581 | [9 empty] | 3.aste | -0.0036182 | 0.49438 | -18.5258 | 232.5588 |  |  | Rajoitus | 22.2623 | W | 516 | W
7,5V | -0.0053125 | 0.44481 | 359.5985
| 5V | [11 empty] | 2.aste | 22.9867 | W
| 2. aste polynomi | [11 empty] | 3.aste | 21.5378 | W
| A | B | C | [9 empty] | KA | 22.2623 | W
| -0.0054076 | 0.38488 | 210.6116
3V
2. aste polynomi
| A | B | C
| -0.0048369 | 0.086518 | 89.919
Verkkokäyrän potenssikäyrän termi (y=ax^2 --> a = y/x^2)
alfa
[19 empty] | 0.13774 | [20 empty] | HUOM Model 250 rajoitettu 7,5 V
[19 empty] | Verkkokäyrä mitoituspisteelle | [20 empty] | Tehostusvara
[19 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Paine puhaltimen yli
[19 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Poisto | Jäte |  | V | l/s | [5 empty] | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella
[19 empty] | 10 | -0.006814 | 1.1894 | 585.3381 | -0.14455 | -59.6527 | 67.8805 | 296.297 | 67.8805 | 634.6753 | 121.337 | 56.9967 | 73.4173 |  | 10 | 67.8805 |  | 581.3448 | Pa |  |  | 91.94% |  |  | TRUE | (OK, jos TOSI)
[19 empty] | 8 | -0.0051982 | 0.42948 | 423.1581 | -0.14294 | -52.9281 | 55.9328 | 296.297 | 55.9328 | 430.9178 | 109.9024 | 51.1298 | 67.9025 |  | 9 | 63.2446 |  | 399.1731 | Pa |  |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[19 empty] | 6 | -0.0054076 | 0.38488 | 210.6116 | -0.14315 | -37.0365 | 39.7252 | 231.4548 | 39.7252 | 217.3672 | 49.9771 | 47.5938 | 61.8174 |  | 8 | 55.9328 |  | 228.0863 | Pa |  |  | 29.6389 | l/s |  | 4.5856 | V
[19 empty] | 4 | -0.0048369 | 0.086518 | 89.919 | -0.14258 | -24.8115 | 25.4183 | 137.7948 | 25.4183 | 88.993 | 21.6614 | 37.7163 | 52.0809 |  | 6 | 39.7252 |  | 94.0019 | Pa |  |  | 121 | Pa
[19 empty] | 7.5 | -0.0053125 | 0.44481 | 359.5985 | -0.14305 | -48.6066 | 51.7161 | 296.297 | 51.7161 | 368.3938 | Model 250 rajoitettu max 7,5 V |  |  |  | 4 | 25.4183 | [8 empty] | Tulos
[42 empty] | 3-9V | 4.5948 | V | T9
[19 empty] | Spektrikorjaukset |  | Lwokt = LwA + K | [20 empty] | 9V - 10V | 1.751 | V | T10
[42 empty] | Kaikki 2. x = l/s, y = Vohj | 4.5674 | V | T11
[21 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[19 empty] | Poistokanava |  | 16 | 13 | 0 | -4 | -9 | -14 | -23 | -32 | ---> | 55.1606 | 52.1606 | 39.1606 | 35.1606 | 30.1606 | 25.1606 | 16.1606 | 7.1606 | 57.0376 | 39.5707 | OK
[19 empty] | Jätekanava |  | 8 | 8 | -1 | -4 | -5 | -10 | -14 | -16 | ----> | 61.3063 | 61.3063 | 52.3063 | 49.3063 | 48.3063 | 43.3063 | 39.3063 | 37.3063 | 64.8574 | 53.2533 | OK
[30 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[22 empty] | A | B | C | [12 empty] | Tehon sovitteet 2. aste polynomi
[21 empty] | 10V | -0.0012978 | 1.9038 | -1.9134 | [13 empty] | A | B | C
[21 empty] | 6,5V | 0.00080725 | 0.52076 | 78.2491 | [12 empty] | 10V | -0.0076219 | 3.1129 | 405.1597
[21 empty] | 5V | 0.0005289 | 0.32101 | 36.3902 | [12 empty] | 6,5V | -0.0057283 | 1.9786 | 306.4277
[21 empty] | 3V | -0.00013773 | 0.23028 | 15.8971 | [12 empty] | 5V | -0.0042805 | 1.0512 | 193.0802
[37 empty] | 3V | -0.0050879 | 0.86559 | 75.2873
Mitatut pisteet
| Poistokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta | [15 empty] | Paine puhaltimen yli
|  | l/s | LwA | P |  | Sovitteet 2. ja 1. aste | [5 empty] | l/s | LwA | P |  | 2. aste tai Lineaarinen | [5 empty] | l/s | W | [13 empty] | Teho vs tilavuusvirta
| 10V | 366.3 | 62.0978 | 515.9924 |  | A | B |  | LwA lask. |  | 10V | 367.2761 | 82.6891 | 515.9924 |  | A | B | C | LwA lask |  | 10V | 180.9218 | 302.3276 | [14 empty] | l/s | Ps puh
|  | 341.4 | 61.4047 | 499.9892 | 2.aste | 0.0001384 | -0.066729 | 67.997 | 64.1051 |  |  | 341.07 | 82.1053 | 499.9892 | 2.aste | -8.8357e-06 | 0.030904 | 72.5508 | 74.6079 |  |  | 223.5792 | 356.5449 | [13 empty] | 10V | 180.9218 | 721.3466
|  | 309.8 | 60.5733 | 457.5489 | Lin. | 0.013453 | 56.8568 |  | 57.77 |  |  | 303.0732 | 81.0802 | 457.5489 | Lineaarinen | 0.025737 | 73.2781 |  | 75.0251 |  |  | 277.7764 | 421.0367 | [14 empty] | 223.5792 | 715.9379
|  | 221 | 60.0131 | 356.5449 | Log | 3.715 | 39.7811 |  | 55.4501 |  |  | 223.5792 | 79.0223 | 356.5449 | Log | 7.3594 | 39.1615 |  | 70.2017 |  |  | 303.0732 | 457.5489 | [14 empty] | 277.7764 | 682.7501
[22 empty] | 344.0085 | 508.8925 | [14 empty] | 303.0732 | 645.1853
| 8V | 304 | 58.3417 | 311.0428 |  | A | B |  |  |  | 8V | 306.4222 | 78.9904 | 311.0428 |  | A | B | C |  |  |  | 367.1836 | 519.4773 | [14 empty] | 344.0085 | 586.0302
|  | 281.7 | 57.3775 | 289.4856 | 2.aste | 0.00017903 | -0.062196 | 60.7001 | 57.7813 |  |  | 280.3754 | 78.0696 | 289.4856 | 2.aste | -2.4722e-05 | 0.048827 | 66.3416 | 68.9954 |  |  | 341.07 | 499.9892 | [14 empty] | 367.1836 | 518.5153
|  | 255.1 | 56.4899 | 260.4799 | Lin. | 0.023251 | 50.9442 |  | 52.2448 |  |  | 247.992 | 76.9423 | 260.4799 | Lineaarinen | 0.036933 | 67.7127 |  | 69.7785 |  |  | 367.2761 | 515.9924 | [14 empty] | 341.07 | 579.6234
|  | 180.1 | 55.305 | 196.9613 | Log | 5.3222 | 27.4828 |  | 48.9 |  |  | 179.9754 | 74.3268 | 196.9613 | Log | 8.6635 | 29.2872 |  | 64.1504 | [18 empty] | 367.2761 | 514.9723
[22 empty] | l/s | W
| 4V | 218.4 | 51.6791 | 130.0214 |  | A | B | C |  |  | 4V | 216.682 | 71.8597 | 130.0214 |  | A | B | C |  |  | 8 V | 142.5403 | 164.9084
|  | 202.3 | 50.4079 | 123.4017 | 2.aste | 0.00043771 | -0.13316 | 59.7363 | 55.1372 |  |  | 203.4805 | 71.0554 | 123.4017 | 2.aste | 0.00012754 | 0.0028071 | 65.2416 | 65.5544 |  |  | 179.9754 | 196.9613 | [14 empty] | l/s | Ps puh
|  | 179.3 | 50.1135 | 110.699 | Lin. | 0.016691 | 47.4721 |  | 48.1351 |  |  | 177.6576 | 69.7857 | 110.699 | Lineaarinen | 0.046552 | 61.6463 |  | 63.4956 |  |  | 225.6806 | 237.8112 | [13 empty] | 8 V | 142.5403 | 473.9139
|  | 128 | 49.839 | 86.5431 | Log | 2.6617 | 36.711 |  | 46.5112 |  |  | 129.3172 | 67.7344 | 86.5431 | Log | 7.7547 | 29.9083 |  | 58.4609 |  |  | 247.992 | 260.4799 | [14 empty] | 179.9754 | 473.1385
[22 empty] | 284.0064 | 292.8625 | [14 empty] | 225.6806 | 462.6971
| 2V | 135.1 | 42.5989 | 45.5376 |  | A | B | C |  |  | 2V | 136.9447 | 61.6361 | 45.5376 |  | A | B | C |  |  |  | 305.1158 | 310.4142 | [14 empty] | 247.992 | 445.0516
|  | 124.4 | 41.7664 | 43.2728 | 2.aste | 0.00084241 | -0.14169 | 46.3623 | 43.3052 |  |  | 126.4833 | 60.7087 | 43.2728 | 2.aste | 0.00037912 | -0.010614 | 55.9817 | 55.9569 |  |  | 280.3754 | 289.4856 | [14 empty] | 284.0064 | 408.5204
|  | 113.2 | 41.1225 | 39.568 | Lin. | 0.035173 | 37.5154 |  | 38.4095 |  |  | 110.482 | 59.4342 | 39.568 | Lineaarinen | 0.070692 | 51.8144 |  | 53.6113 |  |  | 306.4222 | 311.0428 | [14 empty] | 305.1158 | 374.8763
|  | 78.2 | 40.4335 | 33.3093 | Log | 3.5059 | 24.9867 |  | 36.3301 |  |  | 79.6684 | 57.5428 | 33.3093 | Log | 7.3284 | 25.3093 |  | 49.0201 |  |  | 68.2357 | 119.4019
[22 empty] | l/s | W
[21 empty] | 6V | 98.6254 | 73.2555
[22 empty] | 129.3172 | 86.5431 | [14 empty] | l/s | Ps puh
[22 empty] | 160.7795 | 101.629 | [13 empty] | 6V | 98.6254 | 255.3007
[22 empty] | 177.6576 | 110.699 | [14 empty] | 129.3172 | 256.3427
[22 empty] | 203.3412 | 123.3563 | [14 empty] | 160.7795 | 253.8156
[22 empty] | 222.7945 | 134.9092 | [14 empty] | 177.6576 | 243.9319
[22 empty] | 203.4805 | 123.4017 | [14 empty] | 203.3412 | 228.3409
[22 empty] | 216.682 | 130.0214 | [14 empty] | 222.7945 | 215.6986
[22 empty] | l/s | W
[21 empty] | 2V | 60.764 | 29.4094
[22 empty] | 79.6684 | 33.3093 | [14 empty] | l/s | Ps puh
[22 empty] | 98.4635 | 37.2816 | [13 empty] | 4 V | 60.764 | 109.3197
[22 empty] | 110.482 | 39.568 | [14 empty] | 79.6684 | 111.6532
[22 empty] | 128.4554 | 42.9142 | [14 empty] | 98.4635 | 110.4248
[22 empty] | 132.432 | 43.8912 | [14 empty] | 110.482 | 110.0288
[22 empty] | 126.4833 | 43.2728 | [14 empty] | 128.4554 | 102.354
[22 empty] | 136.9447 | 45.5376 | [14 empty] | 132.432 | 100.4856

## Laskenta vaipan läpi 250 (hidden)
Verkkokäyrän positio
Ohjausjännite |  |  | Alfa | Keskiarvo Alfa |  |  |  |  | Tulopuoli | [5 empty] | Poistopuoli | [5 empty] | P* [W] | Äänitehotasot oktaavikaistoittain LW,okt [dB] | [7 empty] | LW,kok** [dB] | LW,A,kok** [dB]
Tulo | 4.621 | V | 0.16 | 0.14887 |  |  |  |  | Ohj.-% [%] | Uohj [V] | qV [dm3/s] | ps21 [Pa] | ps22 [Pa] | ptU [Pa] | Ohj.-% [%] | Uohj [V] | qV [dm3/s] | ps11 [Pa] | ps12 [Pa] | ptU [Pa] |  | 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz
Poisto | 4.3915 | V | 0.13774
[9 empty] | 100 | 9.998 | 345.6 | -64.0289 | 31.7569 | 95.7858 | 100 | 10.001 | 366.1 | -79.0009 | 23.5596 | 102.5605 | 1023.8314 | 69.9444 | 66.4424 | 58.1648 | 45.0338 | 39.5869 | 38.2722 | 38.5175 | 37.5267 | 71.7599 | 54.0521 | 15.8922 | 12.3903 | 4.1126 | -9.0183 | -14.4652 | -15.78 | -15.5347 | -16.5254
Sovite ohj. Jännite vs. LwA vaipan läpi | [8 empty] | 100 | 9.9939 | 295 | -130.367 | 168.8618 | 299.2288 | 100 | 9.9874 | 310.1 | -144.3065 | 158.4418 | 302.7483 | 912.5828 | 68.9346 | 65.0133 | 57.0986 | 43.1252 | 38.5642 | 36.3842 | 37.1594 | 36.0794 | 70.626 | 52.7762 | 16.1584 | 12.2371 | 4.3224 | -9.651 | -14.212 | -16.392 | -15.6168 | -16.6968
y = LwA, x = ohjausjännite | [8 empty] | 100 | 9.9953 | 205.5 | -199.4525 | 297.738 | 497.1905 | 100 | 10.02 | 222.9 | -227.8415 | 277.1562 | 504.9977 | 714.253 | 69.5001 | 66.5305 | 56.5545 | 41.2071 | 37.2126 | 36.6156 | 35.1948 | 34.1264 | 71.4278 | 53.024 | 16.4761 | 13.5065 | 3.5305 | -11.8169 | -15.8114 | -16.4084 | -17.8292 | -18.8976
y = Ax + B | [8 empty] | 80 | 8.003 | 282.1 | -42.324 | 21.2393 | 63.5633 | 80 | 8.0112 | 304.1 | -53.429 | 15.9645 | 69.3935 | 600.7118 | 67.2341 | 62.3012 | 54.1165 | 40.9083 | 36.8914 | 31.8151 | 33.5865 | 32.5033 | 68.6148 | 50.1133 | 17.1208 | 12.1879 | 4.0032 | -9.205 | -13.2219 | -18.2982 | -16.5268 | -17.6101
| A | B | [6 empty] | 80 | 8.0055 | 240.1 | -83.9246 | 110.6915 | 194.6161 | 80 | 8.0048 | 254.15 | -95.7862 | 104.8617 | 200.6478 | 517.977 | 65.936 | 60.6582 | 52.8993 | 39.1307 | 35.1567 | 30.5894 | 32.0392 | 30.6295 | 67.2401 | 48.6564 | 17.2796 | 12.0018 | 4.2429 | -9.5257 | -13.4997 | -18.067 | -16.6171 | -18.0269
Kaikki voltit | 21.5585 | 3.8866 |  | Korjaus, lisätään tulokseen |  |  |  |  | 80 | 7.999 | 169.5 | -127.6412 | 190.7042 | 318.3454 | 80 | 7.9889 | 180 | -149.7172 | 177.4782 | 327.1954 | 396.0153 | 67.2962 | 61.0831 | 51.4439 | 37.437 | 33.9916 | 30.6127 | 28.7984 | 27.7172 | 68.3244 | 48.6471 | 18.6491 | 12.436 | 2.7968 | -11.2101 | -14.6555 | -18.0344 | -19.8487 | -20.9299
VK sijainnin korjaus | -0.57965 | -3.3708 | -2.2667 | -1 | dB |  |  |  | 60 | 5.989 | 199.7 | -23.4594 | 10.9105 | 34.3699 | 60 | 5.994 | 218.2 | -27.4204 | 8.1607 | 35.5811 | 259.3583 | 61.3668 | 55.8849 | 46.9891 | 34.9468 | 30.7222 | 23.7533 | 25.4528 | 23.658 | 62.5832 | 43.3979 | 17.9689 | 12.487 | 3.5912 | -8.4511 | -12.6757 | -19.6446 | -17.9451 | -19.7399
[9 empty] | 60 | 5.9948 | 173.95 | -41.9774 | 55.4741 | 97.4516 | 60 | 6.007 | 182.1 | -49.8585 | 53.0246 | 102.8831 | 220.4973 | 60.6963 | 54.2979 | 44.9778 | 33.4618 | 30.2249 | 23.1949 | 23.2594 | 21.6412 | 61.6974 | 42.038 | 18.6584 | 12.2599 | 2.9398 | -8.5762 | -11.8131 | -18.8431 | -18.7786 | -20.3968
|  |  |  | Ilman korjausta |  | Korjauksen kanssa |  |  | 60 | 6.006 | 128.4 | -62.4018 | 95.9343 | 158.336 | 60 | 6.0003 | 130 | -77.2987 | 89.5195 | 166.8182 | 173.1375 | 61.2758 | 54.2525 | 43.3091 | 31.6846 | 25.6133 | 21.9853 | 20.8571 | 19.0238 | 62.1254 | 41.5223 | 19.7535 | 12.7302 | 1.7868 | -9.8377 | -15.909 | -19.537 | -20.6652 | -22.4985
Maksimi | 4.621 | V | ---> | 36.8841 | dB | 35.8841 | dB
Painotettu keskiarvo | 4.5445 | V | ---> | 36.5243 | dB | 35.5243 | dB | [11 empty] | Verkkokäyränposition korjaus | [12 empty] | 17.5508 | 12.4707 | 3.4807 | -9.6991 | -14.0293 | -17.8894 | -17.7069 | -19.0358
[10 empty] | V | LwA | alfa T | alfa P | alfa KA |  | LwA lask | Erotus |  | Korjaus | LwA Lask korjattu |  | Erotus korj. | [9 empty] | 18 | 12 | 3 | -10 | -14 | -18 | -18 | -19
Korjaus | [9 empty] | 9.998 | 54.0521 | 0.00080196 | 0.00076521 | 0.00078359 |  | 53.5225 | 0.52966 |  | 0.77466 | 54.2972 |  | 0.24501
[10 empty] | 9.9939 | 52.7762 | 0.0034384 | 0.0031483 | 0.0032934 |  | 53.5136 | -0.73744 |  | -0.057589 | 53.4561 |  | 0.67985
Äänitehotasot kanaviin | [9 empty] | 9.9953 | 53.024 | 0.011773 | 0.010164 | 0.010969 |  | 53.5167 | -0.49266 |  | -0.75499 | 52.7617 |  | -0.26233
Imupuoli | Ulko | 45.3929 | dB | [6 empty] | 8.003 | 50.1133 | 0.00079873 | 0.00075039 | 0.00077456 |  | 48.7243 | 1.3891 |  | 0.78138 | 49.5056 |  | -0.60769
| Poisto | 46.4915 | dB | [6 empty] | 8.0055 | 48.6564 | 0.0033759 | 0.0031064 | 0.0032412 |  | 48.731 | -0.074595 |  | -0.048326 | 48.6827 |  | 0.026269
| Erotus | 1.0986 | dB | [6 empty] | 7.999 | 48.6471 | 0.01108 | 0.010099 | 0.01059 |  | 48.7135 | -0.066368 |  | -0.7346 | 47.9789 |  | -0.66823
[10 empty] | 5.989 | 43.3979 | 0.00086183 | 0.00074733 | 0.00080458 |  | 42.4746 | 0.92327 |  | 0.75934 | 43.234 |  | -0.16393
Painepuoli | Tulo | 60.2158 | dB | [6 empty] | 5.9948 | 42.038 | 0.0032206 | 0.0031026 | 0.0031616 |  | 42.4955 | -0.45752 |  | -0.033921 | 42.4616 |  | 0.4236
| Jäte | 60.7853 | dB | [6 empty] | 6.006 | 41.5223 | 0.0096039 | 0.0098709 | 0.0097374 |  | 42.5357 | -1.0134 |  | -0.68597 | 41.8498 |  | 0.32745
| Erotus | 0.56953 | dB | [15 empty] | Verkkokäyräposition korjaus
[10 empty] | Logaritmisovite Vohj vs LwA | [8 empty] | -0.57965 | -3.3708 |  | 0.37826 | dB
Keskiarvo erotus | 0.83409 | dB | [7 empty] | 21.5585 | 3.8866
Korjaus K | 4.5761 | dB | [16 empty] | Max | Min
[19 empty] | 1 | -1
Taustamelukorjattu | 40.4602 | dB
Maksimikorjaus | 33.2841 | dB
|  |  |  | LpA10m2 | LpA2,5m2
Valinta | 35.5243 | dB |  | 31.5449 | 37.5655
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 18 | 12 | 3 | -10 | -14 | -18 | -18 | -19 | ---> | 53.5243 | 47.5243 | 38.5243 | 25.5243 | 21.5243 | 17.5243 | 17.5243 | 16.5243 | 54.6158 | 35.3203 |  | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta vesipatteri 250 (hidden)
|  |  |  | Syötettävät tiedot |  |  | Reynolds-luvun vaikutus korjattavaan lämpötilaeroon
|  |  |  | Tilavuusvirta | 25 | dm3/s
|  |  |  | Tarvittava teho | 570 | W | Tilavuusvirta | Reynolds | Korjaus lämpötilaeroon
|  |  |  | Patterille tulevan ilman lämpötila | 1 | °C | 50 | 3256.3317 | -0.58214
|  |  |  | Patterilta lähtevän ilman lämpötila | 20 | °C | 50 | 4035.0197 | 0.25823 | 0.00032523 | -1.3896
|  |  |  | Menoveden lämpötila | 50 | °C | 50 | 6371.0838 | 0.5986
|  |  |  | Paluuveden lämpötila | 30 | °C | 50 | 1061.8473 | -12.8005 | Korjaus | -0.99587
|  |  |  | Arvio Reynolds-luvusta | 1210.5059 | - | 50
|  |  |  | Tarvittava lämpötilaero patterilla | 11.9852 | K | 50
50
|  |  |  | Patterimitoitus menoveden lämpötilan mukaan |  |  | 100 | 4813.7078 | -2.3334
|  |  |  | Menoveden lämpötila | 50 | °C | 100 | 6158.7144 | -0.019656 | 0.0010308 | -6.8922
Virhetilanne |  | TRUE | FALSE | Paluuveden lämpötila | -5.0297 | °C | 100 | 10618.473 | 3.9313
|  | FALSE |  | Virtaama | 0.0024745 | dm3/s | 100 | 1274.2168 | -15.6765 | Korjaus | -5.6445
|  | FALSE |  | Painehäviö | 0.017953 | kPa | 100
|  | FALSE |  | Painehäviö säätövent (KV=1,00) | 0.0079353 | kPa | 100 | [5 empty] | Korjaus lämpötilaeroon
|  | TRUE |  | Virtausnopeus | 0.020164 | m/s | 100
| VIRHE | TRUE |  | Reynolds | 439.9467 | - | 100 | [5 empty] | -0.99587
[7 empty] | 200 | 7503.7209 | -0.58779
|  |  |  | Patterimitoitus paluuveden lämpötilan mukaan |  |  | 200 | 9768.9952 | 2.1785 | 0.00088764 | -8.6805 |  | 50 | -0.99587
Virhetilanne |  | FALSE | TRUE | Menoveden lämpötila | 14.9703 | °C | 200 | 16140.079 | 4.1257 |  |  |  | 100 | -5.6445
|  | FALSE |  | Paluuveden lämpötila | 30 | °C | 200 | 3610.2808 | -7.5753 | Korjaus | -7.606 |  | 200 | -7.606
|  |  |  | Virtaama | -0.00906 | dm3/s | 200 | [5 empty] | 300 | -7.2381
|  | TRUE |  | Painehäviö | #NUM! | kPa | 200
|  | TRUE |  | Painehäviö säätövent (KV=1,00) | 0.10638 | kPa | 200 | [5 empty] | -0.022119 | -1.7767
|  | TRUE |  | Virtausnopeus | -0.073827 | m/s | 200
| VIRHE | TRUE |  | Reynolds | -1610.8228 | - | 300 | 9202.6766 | -0.20012 |  |  |  | 0.00022319 | -0.10061 | 3.0275
[7 empty] | 300 | 11467.9509 | 0.54913 | 0.00067764 | -8.0584
[7 empty] | 300 | 19962.7293 | 4.6168
[7 empty] | 300 | 4672.1281 | -6.4985 | Korjaus | -7.2381
300
300
300
300
Tarvittavan lämpötilaeron laskenta
[7 empty] | Tilavuusvirta | Kerroin |  | Eksponenttisovite
[7 empty] | 50 | 0.064939 |  | 0.44216 | -4.4629 | 0.011528
[7 empty] | 100 | 0.087931 |  | 0.047851
[7 empty] | 200 | 0.12209
[7 empty] | 300 | 0.14192 |  | 3-asteen polynomin sovite
[10 empty] | 2.9107e-10 | -8.9054e-07 | 0.00058833 | 0.037712
0.051869
Nestepuolen painehäviö
[7 empty] | 1.6827 | 6.0793 | 436.7227

## Laskenta tulopuoli 350 (hidden)
Paine puhaltimen yli (2. aste polyn)
Tuloilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste | [5 empty] | 0.092871 | 3.9263 | -38.9824 |  |  |  | Paine puh. yli | 117.2201 | Pa | [20 empty] | ILMAN PATTERIA
[7 empty] | 25 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten | [11 empty] | SFPINT -LASKENTA | [5 empty] | 10V | -0.0063124 | 0.63458 | 646.4254
y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V | [11 empty] | 8V | -0.0058938 | 0.41705 | 424.6537
x = til.virta | [12 empty] | 20.0151 | -25.3199 | Ulko |  |  | ----> | Ulko | 39.1062 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s |  |  |  |  | Suodatinkorjaus | 0 |  |  |  |  | 6V | -0.006901 | 0.58828 | 199.2324
10V | [12 empty] | 18.6102 | -3.6234 | Tulo |  |  | ----> | Tulo | 56.2805 | dB |  |  | 25 | 368.0233 | 20 | 299.783 | 10 | 213.6134 | 10 | 122.8515 |  |  |  |  | Tuloilman lämpötilahyötysuhde | 79.56% | 25.10.2024 (JU+JK), vertailuilmavirran kennon arvo |  |  |  | 4V | -0.0045287 | -0.1767 | 100.0578
2. aste polynomi | [23 empty] | 100 | 348.743 | 50 | 289.9756 | 50 | 195.729 | 20 | 114.8725 |  |  |  |  | Nimellisilmavirta | 194.4444 |  |  |  |  | PATTERIN KANSSA
A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos | [6 empty] | 200 | 320.9076 | 100 | 272.7309 | 90 | 175.4582 | 40 | 97.2905 |  |  |  |  | Tulopuhaltimen paine-ero | 117.2201 | Pa |  |  |  | 10V | -0.0063692 | 0.61219 | 647.1064
-0.0063124 | 0.63458 | 646.4254 | [10 empty] | 3-9V | 6.9344 | -4.1549 |  | 4.2044 | ---> | Tulopuhallin | 4.1973 | V | OK |  | 300 | 289.86 | 150 | 254.131 | 130 | 151.4758 | 60 | 76.5423 |  |  |  |  | Poistopuhaltimen paine-ero | 108.0444 | Pa |  |  |  | 8V | -0.0059568 | 0.39696 | 425.1453
[13 empty] | 9V - 10V | 6.0269 | 4.0128 |  | 3.4823 |  |  | FALSE |  |  |  | 400 | 254.1377 | 230 | 220.5245 | 170 | 120.4219 | 80 | 49.8423 | [10 empty] | 6V | -0.0069707 | 0.56997 | 199.6307
8V | [12 empty] | Kaikki 2. x = l/s, y = Vohj | -3.6479e-05 | 0.15 | 0.45584 | 4.183 |  | Minimi qV | 40 | l/s |  |  | 500 | 210.6472 | 320 | 173.2505 | 205 | 73.943 | [6 empty] | Tulopuhaltimen hyötysuhde | 12.31% |  |  |  |  | 4V | -0.0046179 | -0.19088 | 100.2451
2. aste polynomi | [12 empty] | Polynomisovite teholle | [10 empty] | 610 | 141.3511 | 395 | 114.6459 | [8 empty] | Poistopuhaltimen hyötysuhde | 13.08%
A | B | C | [9 empty] | 2.aste | 0.082273 | -3.1231 | 50.5324 |  |  | ----> | Tulopuhallin | 23.8021 | W | max | [19 empty] | Onko patteri?
-0.0058938 | 0.41705 | 424.6537 | [9 empty] | 3.aste | 0.00070062 | -0.010648 | 0.73353 | 1.0986 |  |  | Rajoitus | 23.8021 | W | 516 | W | [12 empty] | SFP_int_limit | 1267.6333 |  |  |  |  | FALSE
6V | [11 empty] | 2.aste | 23.8749 | W |  |  |  |  | Poistopuhallin | 22.2623 | [15 empty] | SFP_int_tulo | 139.8647 |  |  |  |  | Valinta
2. aste polynomi | [11 empty] | 3.aste | 23.7293 | W |  |  |  |  | Elektroniikka | 2.37 | [15 empty] | SFP_int_poisto | 61.5164 |  |  |  |  | 10V | -0.0063124 | 0.63458 | 646.4254
A | B | C | [9 empty] | KA | 23.8021 | W | [21 empty] | SFP_int_KOK | 201.3811 |  |  |  |  | 8V | -0.0058938 | 0.41705 | 424.6537
-0.006901 | 0.58828 | 199.2324 | [16 empty] | Total power | 48.4343 | W | [20 empty] | 6V | -0.006901 | 0.58828 | 199.2324
[42 empty] | 4V | -0.0045287 | -0.1767 | 100.0578
4V | [11 empty] | Validointipiste | [6 empty] | Maks qV | 26.9444 | l/s
2. aste polynomi | [11 empty] | 165 | l/s | [5 empty] | SFP | 1.7976 | kW/m3/s
A | B | C | [9 empty] | 198 | Pa
-0.0045287 | -0.1767 | 100.0578
Verkkokäyrän potenssikäyrän termi (y=ax^2 --> a = y/x^2)
alfa
0.16
[18 empty] | Verkkokäyrä mitoituspisteelle | [19 empty] | Tehostusvara
[18 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Paine puhaltimen yli | [7 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos
[18 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  |  |  |  | Maksimi tehostusvara |  | Tarkistus onko käyttöalueella |  |  | 3-9V | 6.9344 | -4.1549 |  | 4.5649
[18 empty] | 10 | -0.0063124 | 0.63458 | 646.4254 | -0.16631 | -60.4657 | 64.2813 | 368.0233 | 64.2813 | 661.1332 | 190.3508 | 58.687 | 73.7223 |  | 10 | 64.2813 |  | 599.4104 | Pa |  | 157.1% |  | TRUE | (OK, jos TOSI) |  | 9V - 10V | 6.0269 | 4.0128 |  | 3.8971
[18 empty] | 8 | -0.0058938 | 0.41705 | 424.6537 | -0.16589 | -49.353 | 51.867 | 299.783 | 51.867 | 430.4293 | 108.2599 | 52.2965 | 69.4975 |  | 9 | 58.2544 |  | 408.6327 | Pa |  | Haluttu tehostuspiste |  | Tehostuspisteen ohjausjännite |  |  | Kaikki 2. x = l/s, y = Vohj | -3.6479e-05 | 0.15 | 0.45584 | 4.5532
[18 empty] | 6 | -0.006901 | 0.58828 | 199.2324 | -0.1669 | -32.8327 | 36.3575 | 213.6134 | 36.3575 | 211.4986 | 47.365 | 47.625 | 64.2504 |  | 8 | 51.867 |  | 232.4532 | Pa |  | 27.5 | l/s | 4.561 | V
[18 empty] | 4 | -0.0045287 | -0.1767 | 100.0578 | -0.16453 | -25.2035 | 24.1295 | 122.8515 | 24.1295 | 93.1572 | 22.4419 | 38.1124 | 55.1192 |  | 6 | 36.3575 |  | 107.5278 | Pa |  | 121 | Pa
[32 empty] | 4 | 24.1295
[18 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[20 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[18 empty] | Ulkokanava |  | 15 | 13 | 1 | -5 | -9 | -14 | -24 | -29 | ---> | 54.1062 | 52.1062 | 40.1062 | 34.1062 | 30.1062 | 25.1062 | 15.1062 | 10.1062 | 56.3752 | 39.4208 | OK
[18 empty] | Tulokanava |  | 6 | 8 | -1 | -4 | -5 | -10 | -14 | -16 | ----> | 62.2805 | 64.2805 | 55.2805 | 52.2805 | 51.2805 | 46.2805 | 42.2805 | 40.2805 | 67.0593 | 56.2029 | OK
[29 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[21 empty] | A | B | C | [12 empty] | Tehon sovitteet 2. aste polynomi
[20 empty] | 10V | 0.00037769 | 0.95964 | 127.1033 | [13 empty] | A | B | C
[20 empty] | 6,5V | 0.00058205 | 0.59865 | 75.6441 | [12 empty] | 10V | -0.0078887 | 3.1314 | 430.7164
[20 empty] | 5V | 0.000119 | 0.44802 | 30.9188 | [12 empty] | 6,5V | -0.0067204 | 2.2461 | 310.2146
[20 empty] | 3V | 7.844e-05 | 0.19954 | 17.5814 | [12 empty] | 5V | -0.0055201 | 1.3814 | 189.5261
[36 empty] | 3V | -0.003047 | 0.51216 | 96.9437
Mitatut pisteet
Ulkokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta | [15 empty] | Paine puhaltimen yli
| l/s | LwA | P |  | Sovitteet 2. ja 1. aste ja logaritmi | [5 empty] | l/s | LwA | P |  | Sovitteet 2. ja 1. aste ja logaritmi | [5 empty] | l/s | W | [13 empty] | Teho vs tilavuusvirta
10V | 344.7 | 62.1447 | 504.4911 |  | A | B |  | LwA lask. |  | 10V | 347.5588 | 81.8515 | 500.7667 |  | A | B | C | LwA lask |  | 10V | 149.9263 | 269.8713 | [14 empty] | l/s | Ps puh
| 324 | 61.1108 | 469.6243 | 2.aste | 0.0001316 | -0.06156 | 67.5623 | 64.1489 |  |  | 318.5737 | 81.0641 | 470.189 | 2.aste | 4.3666e-05 | -0.00025165 | 76.6781 | 76.8423 |  |  | 207.4229 | 344.2411 | [13 empty] | 10V | 149.9263 | 722.4261
| 292.5 | 60.9854 | 439.4751 | Lin. | 0.0090497 | 58.5587 |  | 59.1404 |  |  | 289.3128 | 80.2368 | 441.0612 | Lineaarinen | 0.023651 | 73.5392 |  | 75.0595 |  |  | 261.1074 | 404.7493 | [14 empty] | 207.4229 | 739.5303
| 199.8 | 60.5004 | 336.6081 | Log | 2.2906 | 48.2439 |  | 57.7803 |  |  | 207.4229 | 78.5071 | 345.3257 | Log | 6.2824 | 44.8927 |  | 71.0479 |  |  | 289.3128 | 441.2144 | [14 empty] | 261.1074 | 717.8806
[21 empty] | 320.5409 | 476.0109 | [14 empty] | 289.3128 | 675.419
8V | 281.5 | 58.2423 | 289.3769 |  | A | B |  |  |  | 8V | 283.9677 | 77.7354 | 293.3694 |  | A | B | C |  |  |  | 348.7793 | 508.6455 | [14 empty] | 320.5409 | 623.2369
| 263.3 | 57.7216 | 271.2288 | 2.aste | 6.9042e-05 | -0.0089937 | 55.303 | 55.0223 |  |  | 261.9698 | 76.8629 | 272.8589 | 2.aste | 8.8478e-05 | -0.010385 | 73.538 | 73.2373 |  |  | 318.5737 | 470.2501 | [14 empty] | 348.7793 | 572.2875
| 237.6 | 57.0637 | 247.399 | Lin. | 0.021305 | 52.1378 |  | 53.2428 |  |  | 234.5567 | 75.9863 | 250.0643 | Lineaarinen | 0.029049 | 69.3314 |  | 70.8381 |  |  | 347.5588 | 500.7054 | [14 empty] | 318.5737 | 618.0453
| 163.8 | 55.6823 | 188.5718 | Log | 4.5249 | 32.5365 |  | 50.4038 |  |  | 167.4512 | 74.2778 | 194.6131 | Log | 6.2654 | 42.0763 |  | 66.8163 |  |  | 88.3954 | 219.5172 | [14 empty] | 347.5588 | 562.7672
[37 empty] | 88.3954 | 748.2212
4V | 199.7 | 52.0546 | 128.6916 |  | A | B | C |  |  | 4V | 196.5959 | 70.2945 | 120.3465 |  | A | B | C |  |  |  | l/s | W
| 189.6 | 50.8778 | 112.5589 | 2.aste | 0.00065254 | -0.18352 | 62.5137 | 56.704 |  |  | 188.2497 | 70.3939 | 121.4732 | 2.aste | 6.1523e-05 | 0.012551 | 65.609 | 66.1466 |  | 8 V | 117.9562 | 149.6922 | [14 empty] | l/s | Ps puh
| 172.1 | 50.4007 | 106.1296 | Lin. | 0.01969 | 47.4936 |  | 48.2095 |  |  | 164.3849 | 69.2385 | 108.1734 | Lineaarinen | 0.031871 | 64.1536 |  | 65.3124 |  |  | 167.4512 | 194.213 | [13 empty] | 8 V | 117.9562 | 480.4774
| 116.3 | 49.9852 | 85.3268 | Log | 2.8809 | 36.1037 |  | 46.456 |  |  | 119.6571 | 68.0057 | 85.8109 | Log | 4.8784 | 44.5964 |  | 62.1264 |  |  | 209.8673 | 226.8631 | [14 empty] | 167.4512 | 499.2532
[21 empty] | 234.5567 | 250.0149 | [14 empty] | 209.8673 | 489.6027
2V | 120.9 | 42.7142 | 42.3082 |  | A | B | C |  |  | 2V | 120.0669 | 60.2774 | 42.2554 |  | A | B | C |  |  |  | 285.0541 | 291.7599 | [14 empty] | 234.5567 | 465.3622
| 111.7 | 41.5822 | 40.4953 | 2.aste | 0.0019023 | -0.33292 | 55.1219 | 48.1964 |  |  | 110.2138 | 59.7453 | 41.1737 |  | 0.00032825 | -0.017145 | 57.6158 | 57.3932 |  |  | 262.7163 | 272.3613 | [14 empty] | 285.0541 | 405.8321
| 102.2 | 41.0263 | 37.4605 | Lin. | 0.035781 | 37.8686 |  | 38.7319 |  |  | 101.5421 | 59.2375 | 38.9035 | Lineaarinen | 0.044751 | 54.8202 |  | 55.9 |  |  | 261.9698 | 272.8671 | [14 empty] | 262.7163 | 432.6514
| 75.4 | 40.8288 | 31.8561 | Log | 3.2581 | 26.5015 |  | 36.8733 |  |  | 71.5108 | 58.0702 | 32.2842 | Log | 4.0906 | 40.5355 |  | 53.5577 |  |  | 283.9677 | 293.3486 | [14 empty] | 261.9698 | 433.6376
[21 empty] | 69.7466 | 122.3434 | [14 empty] | 283.9677 | 410.0083
[21 empty] | l/s | W
[20 empty] | 6V | 81.2767 | 68.3381 | [14 empty] | l/s | Ps puh
[21 empty] | 119.6571 | 85.8179 | [13 empty] | 6V | 81.2767 | 265.005
[21 empty] | 150.5971 | 100.5821 | [14 empty] | 119.6571 | 275.7212
[21 empty] | 164.3849 | 108.185 | [14 empty] | 150.5971 | 277.9894
[21 empty] | 191.8027 | 122.0671 | [14 empty] | 164.3849 | 260.1718
[21 empty] | 202.1015 | 127.0358 | [14 empty] | 191.8027 | 256.3865
[21 empty] | 188.2497 | 121.4744 | [14 empty] | 202.1015 | 247.7545
[21 empty] | 196.5959 | 120.3453 | [14 empty] | 188.2497 | 256.2777
[37 empty] | 196.5959 | 237.9663
[21 empty] | l/s | W
[20 empty] | 4V | 49.9063 | 27.7891 | [14 empty] | l/s | Ps puh
[21 empty] | 71.5108 | 32.2847 | [13 empty] | ¤ V | 49.9063 | 115.4382
[21 empty] | 90.0432 | 35.6402 | [14 empty] | 71.5108 | 116.497
[21 empty] | 101.5421 | 38.9023 | [14 empty] | 90.0432 | 119.1784
[21 empty] | 119.0326 | 42.4215 | [14 empty] | 101.5421 | 118.075
[21 empty] | 110.2138 | 41.1739 | [14 empty] | 119.0326 | 114.8876
[21 empty] | 120.0669 | 42.2551 | [14 empty] | 110.2138 | 116.4471
[37 empty] | 120.0669 | 113.8894

## Laskenta poistopuoli 350 (hidden)
Paine puhaltimen yli (2. aste polyn)
Poistoilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste | [5 empty] | 0.095392 | 2.4304 | -26.6976 |  |  |  | Paine puh. yli | 108.0444 | Pa
[7 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [12 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 8 V |  | 6 V |  | 4 V
x = til.virta | [12 empty] | 18.5431 | -21.9163 | Poisto |  |  | ----> | Poisto | 39.1606 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [12 empty] | 21.1631 | -16.4004 | Jäte |  |  | ----> | Jäte | 53.3063 | dB |  |  | 25 | 387.0243 | 20 | 322.8487 | 10 | 231.4548 | 10 | 137.7948
2. aste polynomi | [23 empty] | 100 | 368.0647 | 50 | 312.4056 | 50 | 211.5621 | 20 | 129.5056
A | B | C | [10 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos | [6 empty] | 200 | 340.5875 | 100 | 294.0433 | 90 | 189.1132 | 40 | 110.9257
-0.006814 | 1.1894 | 585.3381 | [10 empty] | 3-9V | 7.6286 | -5.4129 |  | 4.2416 | ---> | Poistopuhallin | 4.2384 | V | OK |  | 300 | 309.742 | 150 | 274.2379 | 130 | 162.7615 | 60 | 88.0985
[13 empty] | 9V - 10V | 4.6359 | 21.5217 |  | 1.1697 |  |  | FALSE |  |  |  | 400 | 273.8652 | 170 | 265.827 | 170 | 129.2695 | 80 | 55.1025
6,5V | [12 empty] | Kaikki 2. x = l/s, y = Vohj | 0.00039243 | 0.10228 | 1.1912 | 4.232 |  | Minimi qV | 40 | l/s |  |  | 500 | 229.1915 | 190 | 257.0886 | 200 | 92.4087
2. aste polynomi | [12 empty] | Polynomisovite teholle | [10 empty] | 580 | 178.9257 | 380 | 141.356
A | B | C | [9 empty] | 2.aste | -0.011711 | 3.6163 | -65.9507 |  |  | ----> | Poistopuhallin | 22.2623 | W | max
-0.0051982 | 0.42948 | 423.1581 | [9 empty] | 3.aste | -0.0036182 | 0.49438 | -18.5258 | 232.5588 |  |  | Rajoitus | 22.2623 | W | 516 | W
5V | [11 empty] | 2.aste | 22.9867 | W
2. aste polynomi | [11 empty] | 3.aste | 21.5378 | W
A | B | C | [9 empty] | KA | 22.2623 | W
-0.0054076 | 0.38488 | 210.6116
3V
2. aste polynomi
A | B | C
-0.0048369 | 0.086518 | 89.919
Verkkokäyrän potenssikäyrän termi (y=ax^2 --> a = y/x^2)
alfa
0.13774
[18 empty] | Verkkokäyrä mitoituspisteelle | [19 empty] | Tehostusvara
[18 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite |  |  | Paine puhaltimen yli | [6 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) |  |  |  | Tulos
[18 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Poisto | Jäte |  | V | l/s |  |  |  |  | Maksimi tehostusvara |  | Tarkistus onko käyttöalueella |  | 3-9V | 7.6286 | -5.4129 |  | 4.5948
[18 empty] | 10 | -0.006814 | 1.1894 | 585.3381 | -0.14455 | -59.6527 | 67.8805 | 387.0243 | 67.8805 | 634.6753 | 121.337 | 56.9967 | 73.4173 |  | 10 | 67.8805 |  | 581.3448 | Pa |  | 151.9% |  | TRUE | (OK, jos TOSI) | 9V - 10V | 4.6359 | 21.5217 |  | 1.751
[18 empty] | 8 | -0.0051982 | 0.42948 | 423.1581 | -0.14294 | -52.9281 | 55.9328 | 322.8487 | 55.9328 | 430.9178 | 109.9024 | 51.1298 | 67.9025 |  | 9 | 63.2446 |  | 399.1731 | Pa |  | Haluttu tehostuspiste |  | Tehostuspisteen ohjausjännite |  | Kaikki 2. x = l/s, y = Vohj | 0.00039243 | 0.10228 | 1.1912 | 4.5674
[18 empty] | 6 | -0.0054076 | 0.38488 | 210.6116 | -0.14315 | -37.0365 | 39.7252 | 231.4548 | 39.7252 | 217.3672 | 49.9771 | 47.5938 | 61.8174 |  | 8 | 55.9328 |  | 228.0863 | Pa |  | 29.6389 | l/s | 4.5856 | V
[18 empty] | 4 | -0.0048369 | 0.086518 | 89.919 | -0.14258 | -24.8115 | 25.4183 | 137.7948 | 25.4183 | 88.993 | 21.6614 | 37.7163 | 52.0809 |  | 6 | 39.7252 |  | 94.0019 | Pa |  | 121 | Pa
[32 empty] | 4 | 25.4183
[18 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[20 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[18 empty] | Poistokanava |  | 16 | 13 | 0 | -4 | -9 | -14 | -23 | -32 | ---> | 55.1606 | 52.1606 | 39.1606 | 35.1606 | 30.1606 | 25.1606 | 16.1606 | 7.1606 | 57.0376 | 39.5707 | OK
[18 empty] | Jätekanava |  | 8 | 8 | -1 | -4 | -5 | -10 | -14 | -16 | ----> | 61.3063 | 61.3063 | 52.3063 | 49.3063 | 48.3063 | 43.3063 | 39.3063 | 37.3063 | 64.8574 | 53.2533 | OK
[29 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[21 empty] | A | B | C | [12 empty] | Tehon sovitteet 2. aste polynomi
[20 empty] | 10V | -0.0012978 | 1.9038 | -1.9134 | [13 empty] | A | B | C
[20 empty] | 6,5V | 0.00080725 | 0.52076 | 78.2491 | [12 empty] | 10V | -0.0076219 | 3.1129 | 405.1597
[20 empty] | 5V | 0.0005289 | 0.32101 | 36.3902 | [12 empty] | 6,5V | -0.0057283 | 1.9786 | 306.4277
[20 empty] | 3V | -0.00013773 | 0.23028 | 15.8971 | [12 empty] | 5V | -0.0042805 | 1.0512 | 193.0802
[36 empty] | 3V | -0.0050879 | 0.86559 | 75.2873
Mitatut pisteet
Poistokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta | [15 empty] | Paine puhaltimen yli
| l/s | LwA | P |  | Sovitteet 2. ja 1. aste | [5 empty] | l/s | LwA | P |  | 2. aste tai Lineaarinen | [5 empty] | l/s | W | [13 empty] | Teho vs tilavuusvirta
10V | 366.3 | 62.0978 | 515.9924 |  | A | B |  | LwA lask. |  | 10V | 367.2761 | 82.6891 | 515.9924 |  | A | B | C | LwA lask |  | 10V | 180.9218 | 302.3276 | [14 empty] | l/s | Ps puh
| 341.4 | 61.4047 | 499.9892 | 2.aste | 0.0001384 | -0.066729 | 67.997 | 64.1051 |  |  | 341.07 | 82.1053 | 499.9892 | 2.aste | -8.8357e-06 | 0.030904 | 72.5508 | 74.6079 |  |  | 223.5792 | 356.5449 | [13 empty] | 10V | 180.9218 | 721.3466
| 309.8 | 60.5733 | 457.5489 | Lin. | 0.013453 | 56.8568 |  | 57.77 |  |  | 303.0732 | 81.0802 | 457.5489 | Lineaarinen | 0.025737 | 73.2781 |  | 75.0251 |  |  | 277.7764 | 421.0367 | [14 empty] | 223.5792 | 715.9379
| 221 | 60.0131 | 356.5449 | Log | 3.715 | 39.7811 |  | 55.4501 |  |  | 223.5792 | 79.0223 | 356.5449 | Log | 7.3594 | 39.1615 |  | 70.2017 |  |  | 303.0732 | 457.5489 | [14 empty] | 277.7764 | 682.7501
[21 empty] | 344.0085 | 508.8925 | [14 empty] | 303.0732 | 645.1853
8V | 304 | 58.3417 | 311.0428 |  | A | B |  |  |  | 8V | 306.4222 | 78.9904 | 311.0428 |  | A | B | C |  |  |  | 367.1836 | 519.4773 | [14 empty] | 344.0085 | 586.0302
| 281.7 | 57.3775 | 289.4856 | 2.aste | 0.00017903 | -0.062196 | 60.7001 | 57.7813 |  |  | 280.3754 | 78.0696 | 289.4856 | 2.aste | -2.4722e-05 | 0.048827 | 66.3416 | 68.9954 |  |  | 341.07 | 499.9892 | [14 empty] | 367.1836 | 518.5153
| 255.1 | 56.4899 | 260.4799 | Lin. | 0.023251 | 50.9442 |  | 52.2448 |  |  | 247.992 | 76.9423 | 260.4799 | Lineaarinen | 0.036933 | 67.7127 |  | 69.7785 |  |  | 367.2761 | 515.9924 | [14 empty] | 341.07 | 579.6234
| 180.1 | 55.305 | 196.9613 | Log | 5.3222 | 27.4828 |  | 48.9 |  |  | 179.9754 | 74.3268 | 196.9613 | Log | 8.6635 | 29.2872 |  | 64.1504 | [18 empty] | 367.2761 | 514.9723
[21 empty] | l/s | W
4V | 218.4 | 51.6791 | 130.0214 |  | A | B | C |  |  | 4V | 216.682 | 71.8597 | 130.0214 |  | A | B | C |  |  | 8 V | 142.5403 | 164.9084
| 202.3 | 50.4079 | 123.4017 | 2.aste | 0.00043771 | -0.13316 | 59.7363 | 55.1372 |  |  | 203.4805 | 71.0554 | 123.4017 | 2.aste | 0.00012754 | 0.0028071 | 65.2416 | 65.5544 |  |  | 179.9754 | 196.9613 | [14 empty] | l/s | Ps puh
| 179.3 | 50.1135 | 110.699 | Lin. | 0.016691 | 47.4721 |  | 48.1351 |  |  | 177.6576 | 69.7857 | 110.699 | Lineaarinen | 0.046552 | 61.6463 |  | 63.4956 |  |  | 225.6806 | 237.8112 | [13 empty] | 8 V | 142.5403 | 473.9139
| 128 | 49.839 | 86.5431 | Log | 2.6617 | 36.711 |  | 46.5112 |  |  | 129.3172 | 67.7344 | 86.5431 | Log | 7.7547 | 29.9083 |  | 58.4609 |  |  | 247.992 | 260.4799 | [14 empty] | 179.9754 | 473.1385
[21 empty] | 284.0064 | 292.8625 | [14 empty] | 225.6806 | 462.6971
2V | 135.1 | 42.5989 | 45.5376 |  | A | B | C |  |  | 2V | 136.9447 | 61.6361 | 45.5376 |  | A | B | C |  |  |  | 305.1158 | 310.4142 | [14 empty] | 247.992 | 445.0516
| 124.4 | 41.7664 | 43.2728 | 2.aste | 0.00084241 | -0.14169 | 46.3623 | 43.3052 |  |  | 126.4833 | 60.7087 | 43.2728 | 2.aste | 0.00037912 | -0.010614 | 55.9817 | 55.9569 |  |  | 280.3754 | 289.4856 | [14 empty] | 284.0064 | 408.5204
| 113.2 | 41.1225 | 39.568 | Lin. | 0.035173 | 37.5154 |  | 38.4095 |  |  | 110.482 | 59.4342 | 39.568 | Lineaarinen | 0.070692 | 51.8144 |  | 53.6113 |  |  | 306.4222 | 311.0428 | [14 empty] | 305.1158 | 374.8763
| 78.2 | 40.4335 | 33.3093 | Log | 3.5059 | 24.9867 |  | 36.3301 |  |  | 79.6684 | 57.5428 | 33.3093 | Log | 7.3284 | 25.3093 |  | 49.0201 |  |  | 68.2357 | 119.4019
[21 empty] | l/s | W
[20 empty] | 6V | 98.6254 | 73.2555
[21 empty] | 129.3172 | 86.5431 | [14 empty] | l/s | Ps puh
[21 empty] | 160.7795 | 101.629 | [13 empty] | 6V | 98.6254 | 255.3007
[21 empty] | 177.6576 | 110.699 | [14 empty] | 129.3172 | 256.3427
[21 empty] | 203.3412 | 123.3563 | [14 empty] | 160.7795 | 253.8156
[21 empty] | 222.7945 | 134.9092 | [14 empty] | 177.6576 | 243.9319
[21 empty] | 203.4805 | 123.4017 | [14 empty] | 203.3412 | 228.3409
[21 empty] | 216.682 | 130.0214 | [14 empty] | 222.7945 | 215.6986
[21 empty] | l/s | W
[20 empty] | 2V | 60.764 | 29.4094
[21 empty] | 79.6684 | 33.3093 | [14 empty] | l/s | Ps puh
[21 empty] | 98.4635 | 37.2816 | [13 empty] | 4 V | 60.764 | 109.3197
[21 empty] | 110.482 | 39.568 | [14 empty] | 79.6684 | 111.6532
[21 empty] | 128.4554 | 42.9142 | [14 empty] | 98.4635 | 110.4248
[21 empty] | 132.432 | 43.8912 | [14 empty] | 110.482 | 110.0288
[21 empty] | 126.4833 | 43.2728 | [14 empty] | 128.4554 | 102.354
[21 empty] | 136.9447 | 45.5376 | [14 empty] | 132.432 | 100.4856

## Laskenta vaipan läpi 350 (hidden)
Verkkokäyrän positio
Ohjausjännite |  |  | Alfa | Keskiarvo Alfa |  |  |  |  | Tulopuoli | [5 empty] | Poistopuoli | [5 empty] | P* [W] | Äänitehotasot oktaavikaistoittain LW,okt [dB] | [7 empty] | LW,kok** [dB] | LW,A,kok** [dB]
Tulo | 4.621 | V | 0.16 | 0.14887 |  |  |  |  | Ohj.-% [%] | Uohj [V] | qV [dm3/s] | ps21 [Pa] | ps22 [Pa] | ptU [Pa] | Ohj.-% [%] | Uohj [V] | qV [dm3/s] | ps11 [Pa] | ps12 [Pa] | ptU [Pa] |  | 63 Hz | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2 kHz | 4 kHz | 8 kHz
Poisto | 4.3915 | V | 0.13774
[9 empty] | 100 | 9.998 | 345.6 | -64.0289 | 31.7569 | 95.7858 | 100 | 10.001 | 366.1 | -79.0009 | 23.5596 | 102.5605 | 1023.8314 | 69.9444 | 66.4424 | 58.1648 | 45.0338 | 39.5869 | 38.2722 | 38.5175 | 37.5267 | 71.7599 | 54.0521 | 15.8922 | 12.3903 | 4.1126 | -9.0183 | -14.4652 | -15.78 | -15.5347 | -16.5254
Sovite ohj. Jännite vs. LwA vaipan läpi | [8 empty] | 100 | 9.9939 | 295 | -130.367 | 168.8618 | 299.2288 | 100 | 9.9874 | 310.1 | -144.3065 | 158.4418 | 302.7483 | 912.5828 | 68.9346 | 65.0133 | 57.0986 | 43.1252 | 38.5642 | 36.3842 | 37.1594 | 36.0794 | 70.626 | 52.7762 | 16.1584 | 12.2371 | 4.3224 | -9.651 | -14.212 | -16.392 | -15.6168 | -16.6968
y = LwA, x = ohjausjännite | [8 empty] | 100 | 9.9953 | 205.5 | -199.4525 | 297.738 | 497.1905 | 100 | 10.02 | 222.9 | -227.8415 | 277.1562 | 504.9977 | 714.253 | 69.5001 | 66.5305 | 56.5545 | 41.2071 | 37.2126 | 36.6156 | 35.1948 | 34.1264 | 71.4278 | 53.024 | 16.4761 | 13.5065 | 3.5305 | -11.8169 | -15.8114 | -16.4084 | -17.8292 | -18.8976
y = Ax + B | [8 empty] | 80 | 8.003 | 282.1 | -42.324 | 21.2393 | 63.5633 | 80 | 8.0112 | 304.1 | -53.429 | 15.9645 | 69.3935 | 600.7118 | 67.2341 | 62.3012 | 54.1165 | 40.9083 | 36.8914 | 31.8151 | 33.5865 | 32.5033 | 68.6148 | 50.1133 | 17.1208 | 12.1879 | 4.0032 | -9.205 | -13.2219 | -18.2982 | -16.5268 | -17.6101
| A | B | [6 empty] | 80 | 8.0055 | 240.1 | -83.9246 | 110.6915 | 194.6161 | 80 | 8.0048 | 254.15 | -95.7862 | 104.8617 | 200.6478 | 517.977 | 65.936 | 60.6582 | 52.8993 | 39.1307 | 35.1567 | 30.5894 | 32.0392 | 30.6295 | 67.2401 | 48.6564 | 17.2796 | 12.0018 | 4.2429 | -9.5257 | -13.4997 | -18.067 | -16.6171 | -18.0269
Kaikki voltit | 21.5585 | 3.8866 |  | Korjaus, lisätään tulokseen |  |  |  |  | 80 | 7.999 | 169.5 | -127.6412 | 190.7042 | 318.3454 | 80 | 7.9889 | 180 | -149.7172 | 177.4782 | 327.1954 | 396.0153 | 67.2962 | 61.0831 | 51.4439 | 37.437 | 33.9916 | 30.6127 | 28.7984 | 27.7172 | 68.3244 | 48.6471 | 18.6491 | 12.436 | 2.7968 | -11.2101 | -14.6555 | -18.0344 | -19.8487 | -20.9299
VK sijainnin korjaus | -0.57965 | -3.3708 | -2.2667 | -1 | dB |  |  |  | 60 | 5.989 | 199.7 | -23.4594 | 10.9105 | 34.3699 | 60 | 5.994 | 218.2 | -27.4204 | 8.1607 | 35.5811 | 259.3583 | 61.3668 | 55.8849 | 46.9891 | 34.9468 | 30.7222 | 23.7533 | 25.4528 | 23.658 | 62.5832 | 43.3979 | 17.9689 | 12.487 | 3.5912 | -8.4511 | -12.6757 | -19.6446 | -17.9451 | -19.7399
[9 empty] | 60 | 5.9948 | 173.95 | -41.9774 | 55.4741 | 97.4516 | 60 | 6.007 | 182.1 | -49.8585 | 53.0246 | 102.8831 | 220.4973 | 60.6963 | 54.2979 | 44.9778 | 33.4618 | 30.2249 | 23.1949 | 23.2594 | 21.6412 | 61.6974 | 42.038 | 18.6584 | 12.2599 | 2.9398 | -8.5762 | -11.8131 | -18.8431 | -18.7786 | -20.3968
|  |  |  | Ilman korjausta |  | Korjauksen kanssa |  |  | 60 | 6.006 | 128.4 | -62.4018 | 95.9343 | 158.336 | 60 | 6.0003 | 130 | -77.2987 | 89.5195 | 166.8182 | 173.1375 | 61.2758 | 54.2525 | 43.3091 | 31.6846 | 25.6133 | 21.9853 | 20.8571 | 19.0238 | 62.1254 | 41.5223 | 19.7535 | 12.7302 | 1.7868 | -9.8377 | -15.909 | -19.537 | -20.6652 | -22.4985
Maksimi | 4.621 | V | ---> | 36.8841 | dB | 35.8841 | dB
Painotettu keskiarvo | 4.5445 | V | ---> | 36.5243 | dB | 35.5243 | dB | [11 empty] | Verkkokäyränposition korjaus | [12 empty] | 17.5508 | 12.4707 | 3.4807 | -9.6991 | -14.0293 | -17.8894 | -17.7069 | -19.0358
[10 empty] | V | LwA | alfa T | alfa P | alfa KA |  | LwA lask | Erotus |  | Korjaus | LwA Lask korjattu |  | Erotus korj. | [9 empty] | 18 | 12 | 3 | -10 | -14 | -18 | -18 | -19
Korjaus | [9 empty] | 9.998 | 54.0521 | 0.00080196 | 0.00076521 | 0.00078359 |  | 53.5225 | 0.52966 |  | 0.77466 | 54.2972 |  | 0.24501
[10 empty] | 9.9939 | 52.7762 | 0.0034384 | 0.0031483 | 0.0032934 |  | 53.5136 | -0.73744 |  | -0.057589 | 53.4561 |  | 0.67985
Äänitehotasot kanaviin | [9 empty] | 9.9953 | 53.024 | 0.011773 | 0.010164 | 0.010969 |  | 53.5167 | -0.49266 |  | -0.75499 | 52.7617 |  | -0.26233
Imupuoli | Ulko | 45.3929 | dB | [6 empty] | 8.003 | 50.1133 | 0.00079873 | 0.00075039 | 0.00077456 |  | 48.7243 | 1.3891 |  | 0.78138 | 49.5056 |  | -0.60769
| Poisto | 46.4915 | dB | [6 empty] | 8.0055 | 48.6564 | 0.0033759 | 0.0031064 | 0.0032412 |  | 48.731 | -0.074595 |  | -0.048326 | 48.6827 |  | 0.026269
| Erotus | 1.0986 | dB | [6 empty] | 7.999 | 48.6471 | 0.01108 | 0.010099 | 0.01059 |  | 48.7135 | -0.066368 |  | -0.7346 | 47.9789 |  | -0.66823
[10 empty] | 5.989 | 43.3979 | 0.00086183 | 0.00074733 | 0.00080458 |  | 42.4746 | 0.92327 |  | 0.75934 | 43.234 |  | -0.16393
Painepuoli | Tulo | 60.2158 | dB | [6 empty] | 5.9948 | 42.038 | 0.0032206 | 0.0031026 | 0.0031616 |  | 42.4955 | -0.45752 |  | -0.033921 | 42.4616 |  | 0.4236
| Jäte | 60.7853 | dB | [6 empty] | 6.006 | 41.5223 | 0.0096039 | 0.0098709 | 0.0097374 |  | 42.5357 | -1.0134 |  | -0.68597 | 41.8498 |  | 0.32745
| Erotus | 0.56953 | dB | [15 empty] | Verkkokäyräposition korjaus
[10 empty] | Logaritmisovite Vohj vs LwA | [8 empty] | -0.57965 | -3.3708 |  | 0.37826 | dB
Keskiarvo erotus | 0.83409 | dB | [7 empty] | 21.5585 | 3.8866
Korjaus K | 4.5761 | dB | [16 empty] | Max | Min
[19 empty] | 1 | -1
Taustamelukorjattu | 40.4602 | dB
Maksimikorjaus | 33.2841 | dB
|  |  |  | LpA10m2 | LpA2,5m2
Valinta | 35.5243 | dB |  | 31.5449 | 37.5655
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 18 | 12 | 3 | -10 | -14 | -18 | -18 | -19 | ---> | 53.5243 | 47.5243 | 38.5243 | 25.5243 | 21.5243 | 17.5243 | 17.5243 | 16.5243 | 54.6158 | 35.3203 |  | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta tulopuoli 100 (hidden)
Tuloilma tilavuusvirta vs. painehäviö | [5 empty] | Syötä piste
[6 empty] | 25 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [11 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 6,5 V |  | 5 V |  | 3 V
x = til.virta | [11 empty] | 18.5976 | -9.2412 | Ulko |  |  | ----> | Ulko | 50.6221 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 18.7223 | 1.2765 | Tulo |  |  | ----> | Tulo | 61.5412 | dB |  |  | 25 | 105.5599 | 20 | 80.7046 | 10 | 54.339 | 10 | 20.411
2. aste polynomi | [22 empty] | 120 | 91.3341 | 50 | 73.8387 | 40 | 44.8078 | 20 | 15.4146
A | B | C | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 79.8615 | 100 | 61.6656 | 60 | 38.0656 | 25 | 12.8146
-0.022433 | -2.261 | 513.6437 | [9 empty] | 3-7,5V | 6.3648 | -6.71 |  |  | ---> | Tulopuhallin | 4.9821 | V | OK |  | 250 | 69.1547 | 150 | 48.3562 | 80 | 30.9537 | 30 | 10.1388
[12 empty] | 7,5V - 10V | 2.4798 | 22.4272 |  |  |  |  | TRUE |  |  |  | 320 | 55.3015 | 170 | 42.6336 | 100 | 23.4037 | 34 | 7.939
6,5V | [17 empty] | Minimi qV | 18 | l/s | Pulkkasen maili 14.6.19 |  | 390 | 39.3343 | 190 | 36.634 | 110 | 19.4367
2. aste polynomi | [11 empty] | Polynomisovite teholle | [10 empty] | 400 | 36.815 | 220 | 27.0145
A | B | C | [9 empty] | 0.050172 | -1.0384 | 11.44 |  |  | ----> | Tulopuhallin | 16.8363 | W
-0.01376 | -2.2428 | 290.6309 | [15 empty] | Rajoitus | 16.8363 | W
5V | [17 empty] | Poistopuhallin | 15.4596
2. aste polynomi | [17 empty] | Elektroniikka | 3
A | B | C
-0.011131 | -2.0439 | 153.9328 | [15 empty] | Total power | 35.2959 | W
3V | [17 empty] | Maks qV | 26.9444 | l/s
2. aste polynomi | [17 empty] | SFP | 1.3099 | kW/m3/s
A | B | C
-0.010317 | -1.6318 | 47.6053
Verkkokäyrän potenssikäyrän termi
alfa
0.16
[17 empty] | Verkkokäyrä mitoituspisteelle | [16 empty] | Tehostusvara
[17 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite
[17 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella
[17 empty] | 10 | -0.022433 | -2.261 | 513.6437 | -0.18243 | -59.6189 | 47.2252 | 105.5599 | 47.2252 | 356.8358 | 74.6117 | 62.4734 | 73.95 |  | 10 | 47.2252 |  | 88.9% |  |  | TRUE | (OK, jos TOSI)
[17 empty] | 6.5 | -0.01376 | -2.2428 | 290.6309 | -0.17376 | -47.8573 | 34.9497 | 80.7046 | 34.9497 | 195.4367 | 35.3534 | 56.9077 | 67.6176 |  | 7.5 | 41.0257 |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[17 empty] | 5 | -0.011131 | -2.0439 | 153.9328 | -0.17113 | -36.5524 | 24.6086 | 54.339 | 24.6086 | 96.8934 | 17.3569 | 50.2011 | 60.5568 |  | 6.5 | 34.9497 |  | 27.5 | l/s |  | 5.3749 | V
[17 empty] | 3 | -0.010317 | -1.6318 | 47.6053 | -0.17032 | -22.1819 | 12.6008 | 20.411 | 12.6008 | 25.4049 | 5.9921 | 37.9311 | 49.0989 |  | 5 | 24.6086 |  | 121 | Pa
[31 empty] | 3 | 12.6008
[17 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[19 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[17 empty] | Ulkokanava |  | 21 | 10 | 3 | -8 | -20 | -26 | -34 | -39 | ---> | 71.6221 | 60.6221 | 53.6221 | 42.6221 | 30.6221 | 24.6221 | 16.6221 | 11.6221 | 72.0228 | 50.2252 | OK
[17 empty] | Tulokanava |  | 22 | 7 | -1 | -4 | -10 | -12 | -18 | -28 | ----> | 83.5412 | 68.5412 | 60.5412 | 57.5412 | 51.5412 | 49.5412 | 43.5412 | 33.5412 | 83.7127 | 61.5748 | OK
[28 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[20 empty] | A | B | C
[19 empty] | 10V | 0.001102 | 0.4995 | 48.5651
[19 empty] | 6,5V | 0.0033057 | 0.10846 | 27.5248
[19 empty] | 5V | 0.00023977 | 0.20094 | 12.2668
[19 empty] | 3V | -0.0010065 | 0.10696 | 4.8041
Mitatut pisteet
Ulkokanava |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P |  | 3. aste polynomisovitus | [5 empty] | l/s | W
10V | 95.5209 | 60.1803 | 106.6506 | A | B |  |  |  | 10V | 95.4073 | 72.434 | 106.1963 |  | A | B | C |  |  | 10V | 95.5209 | 106.6506
| 78.1727 | 61.4566 | 95.4485 | -0.0010983 | 0.10839 | 59.804 |  |  |  | 77.2191 | 73.082 | 91.7251 |  | -0.00014052 | -0.011427 | 74.8031 |  |  |  | 78.1727 | 95.4485
| 56.9973 | 62.5062 | 80.5375 | [6 empty] | 59.03 | 73.6396 | 82.8554 | [7 empty] | 56.9973 | 80.5375
| 32.7364 | 62.149 | 66.133 | [6 empty] | 38.9982 | 74.1435 | 69.415 | [7 empty] | 32.7364 | 66.133
[20 empty] | 95.4073 | 106.1963
6,5V | 71.5936 | 55.839 | 52.1949 | A | B |  |  |  | 6,5V | 71.9964 | 67.704 | 52.5362 |  | A | B | C |  |  |  | 77.2191 | 91.7251
| 58.1309 | 56.9804 | 45.4648 | -0.0014317 | 0.12589 | 54.2567 |  |  |  | 56.69 | 67.2609 | 43.6681 |  | 0.00037721 | -0.039883 | 68.5508 |  |  |  | 59.03 | 82.8554
| 42.9618 | 56.8139 | 38.6996 | [6 empty] | 44.3245 | 67.7653 | 38.9775 | [7 empty] | 38.9982 | 69.415
| 24.4927 | 56.5384 | 32.0906 | [6 empty] | 29.0309 | 67.6414 | 33.5188 | [7 empty] | l/s | W
[19 empty] | 6,5V | 71.5936 | 52.1949
5V | 48.4536 | 49.7994 | 22.085 | A | B | C |  |  | 5V | 49.2318 | 60.9907 | 23.2492 |  | A | B | C |  |  |  | 58.1309 | 45.4648
| 39.0067 | 50.5413 | 20.3408 | -0.0024813 | 0.16747 | 47.5825 |  |  |  | 40.0727 | 60.9429 | 20.6404 |  | -0.0020467 | 0.16671 | 57.6939 |  |  |  | 24.4927 | 32.0906
| 29.0391 | 50.1731 | 17.7428 | [6 empty] | 30.72 | 61.0168 | 18.9012 | [7 empty] | 71.9964 | 52.5362
| 17.1364 | 49.7747 | 15.7761 | [6 empty] | 19.8573 | 60.1583 | 16.2855 | [7 empty] | 56.69 | 43.6681
[20 empty] | 44.3245 | 38.9775
3V | 21.9036 | 38.6323 | 6.6132 | A | B | C |  |  | 3V | 21.7936 | 49.8135 | 6.6532 |  | A | B | C |  |  |  | 29.0309 | 33.5188
| 19.9791 | 39.3442 | 6.6144 | 0.0046809 | -0.044231 | 37.7452 |  |  |  | 19.1882 | 50.0494 | 6.4973 |  | -0.015285 | 0.61031 | 43.8354 |  |  |  | l/s | W
| 14.3682 | 37.7587 | 6.0286 | [6 empty] | 15.0464 | 49.4685 | 6.2379 | [6 empty] | 5V | 48.4536 | 22.085
| 8.88 | 37.8143 | 5.7833 | [6 empty] | 9.6709 | 48.3298 | 5.7653 | [7 empty] | 39.0067 | 20.3408
[20 empty] | 17.1364 | 15.7761
[20 empty] | 49.2318 | 23.2492
[20 empty] | 40.0727 | 20.6404
[20 empty] | 30.72 | 18.9012
[20 empty] | 19.8573 | 16.2855
[20 empty] | l/s | W
[19 empty] | 3V | 21.9036 | 6.6132
[20 empty] | 19.9791 | 6.6144
[20 empty] | 14.3682 | 6.0286
[20 empty] | 21.7936 | 6.6532
[20 empty] | 19.1882 | 6.4973
[20 empty] | 15.0464 | 6.2379
[20 empty] | 9.6709 | 5.7653

## Laskenta poistopuoli 100 (hidden)
Tuloilma tilavuusvirta vs. painehäviö | [5 empty] | Syötä piste
[6 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [11 empty] | A | B | [5 empty] | LwA |  |  |  | 10 V |  | 6,5 V |  | 5 V |  | 3 V
x = til.virta | [11 empty] | 20.6841 | -19.9459 | Ulko |  |  | ----> | Poisto | 48.183 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 19.4447 | -2.566 | Tulo |  |  | ----> | Jäte | 61.4807 | dB |  |  | 25 | 115.6788 | 20 | 91.9884 | 15 | 63.4949 | 10 | 29.6705
2. aste polynomi | [22 empty] | 120 | 103.494 | 50 | 86.2865 | 40 | 56.9738 | 20 | 22.5789
A | B | C | [9 empty] | Lineaarisovite ohjausjännitteelle (2-osainen) | [10 empty] | 190 | 93.3922 | 100 | 75.9006 | 60 | 51.1452 | 30 | 16.489
-0.03891 | 0.73137 | 461.0714 | [9 empty] | 3-7,5V | 7.1768 | -6.4437 |  |  | ---> | Tulopuhallin | 4.6522 | V | OK |  | 250 | 83.6475 | 150 | 63.979 | 80 | 44.536 | 35 | 13.7083
[12 empty] | 7,5V - 10V | 2.3275 | 29.9256 |  |  |  |  | TRUE |  |  |  | 320 | 70.3402 | 170 | 58.5924 | 100 | 36.7108 | 40 | 11.0677
6,5 V | [17 empty] | Minimi qV | 18 | l/s | Pulkkasen maili 14.6.19 |  | 390 | 53.1577 | 190 | 52.7094 | 125 | 23.2979
2. aste polynomi | [11 empty] | Polynomisovite teholle | [10 empty] | 425 | 41.2632 | 245 | 32.0448
A | B | C | [9 empty] | 0.045067 | -1.1301 | 13.1915 |  |  | ----> | Tulopuhallin | 15.4596 | W
-0.0278 | -0.30539 | 283.3333 | [15 empty] | Rajoitus | 15.4596 | W
5V | [17 empty] | Poistopuhallin | 15.2242
2. aste polynomi | [17 empty] | Elektroniikka | 3
A | B | C
-0.032581 | 0.091237 | 140.5589 | [15 empty] | Total power | 33.6838 | W
3V | [17 empty] | Maks qV | 26.9444 | l/s
2. aste polynomi | [17 empty] | SFP | 1.2501 | kW/m3/s
A | B | C
0.017595 | -2.3295 | 63.6265
Verkkokäyrän potenssikäyrän termi
alfa
0.13774
[17 empty] | Verkkokäyrä mitoituspisteelle | [16 empty] | Tehostusvara
[17 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite
[17 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella
[17 empty] | 10 | -0.03891 | 0.73137 | 461.0714 | -0.17665 | -49.0608 | 53.201 | 115.6788 | 53.201 | 389.8527 | 80.8249 | 62.8351 | 74.8146 |  | 10 | 53.201 |  | 97.45% |  |  | TRUE | (OK, jos TOSI)
[17 empty] | 6.5 | -0.0278 | -0.30539 | 283.3333 | -0.16554 | -42.3037 | 40.4589 | 91.9884 | 40.4589 | 225.4709 | 40.5974 | 56.4921 | 69.2947 |  | 7.5 | 47.3821 |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[17 empty] | 5 | -0.032581 | 0.091237 | 140.5589 | -0.17032 | -28.4607 | 28.9964 | 63.4949 | 28.9964 | 115.811 | 18.9339 | 48.7215 | 62.8396 |  | 6.5 | 40.4589 |  | 29.6389 | l/s |  | 5.0277 | V
[17 empty] | 3 | 0.017595 | -2.3295 | 63.6265 | -0.12015 | -34.6656 | 15.2768 | 29.6705 | 15.2768 | 32.1461 | 6.2643 | 36.9443 | 50.5 |  | 5 | 28.9964 |  | 121 | Pa
[31 empty] | 3 | 15.2768
[17 empty] | Spektrikorjaukset |  | Lwokt = LwA + K
[19 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[17 empty] | Poistokanava |  | 19 | 10 | 3 | -5 | -13 | -19 | -29 | -34 | ---> | 67.183 | 58.183 | 51.183 | 43.183 | 35.183 | 29.183 | 19.183 | 14.183 | 67.8119 | 47.8744 | OK
[17 empty] | Jätekanava |  | 22 | 6 | 3 | -4 | -9 | -11 | -18 | -22 | ----> | 83.4807 | 67.4807 | 64.4807 | 57.4807 | 52.4807 | 50.4807 | 43.4807 | 39.4807 | 83.6579 | 62.2701 | Tarkista laskenta!
[28 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
Tehon sovitteet 2. aste polynomi
[20 empty] | A | B | C
[19 empty] | 10V | 0.0034049 | 0.14582 | 63.4301
[19 empty] | 6,5V | 0.0013762 | 0.30358 | 26.0624
[19 empty] | 5V | -0.00035887 | 0.275 | 11.2616
[19 empty] | 3V | 0.0027577 | -0.041245 | 6.2508
Mitatut pisteet
Poistokanava |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P |  | 3. aste polynomisovitus | [5 empty] | l/s | W
10V | 107.4702 | 61.134 | 116.6287 | A | B |  |  |  | 10V | 104.6208 | 73.3494 | 117.1517 |  | A | B | C |  |  | 10V | 107.4702 | 116.6287
| 97.1646 | 61.4631 | 107.8905 | -0.00046771 | 0.042405 | 61.9028 |  |  |  | 87.7167 | 73.5866 | 108.2515 |  | -0.00020328 | 0.0010982 | 75.3315 |  |  |  | 97.1646 | 107.8905
| 77.4504 | 62.4761 | 92.2331 | [6 empty] | 60.0687 | 74.9037 | 88.1001 | [7 empty] | 77.4504 | 92.2331
| 55.7661 | 62.7869 | 76.4725 | [6 empty] | 38.463 | 74.9824 | 75.6662 | [7 empty] | 55.7661 | 76.4725
[20 empty] | 104.6208 | 117.1517
6,5V | 85.2194 | 56.2268 | 60.5778 | A | B |  |  |  | 6,5V | 81.7942 | 68.6258 | 61.6094 |  | A | B | C |  |  |  | 87.7167 | 108.2515
| 75.3089 | 56.9869 | 55.5276 | -0.00045476 | 0.055462 | 54.9925 |  |  |  | 68.9613 | 68.6928 | 55.2532 |  | -0.00019894 | 0.0062784 | 69.3664 |  |  |  | 60.0687 | 88.1001
| 59.0911 | 56.3872 | 45.261 | [6 empty] | 46.5991 | 69.3626 | 44.8711 | [7 empty] | 38.463 | 75.6662
| 42.1776 | 56.6104 | 37.7649 | [6 empty] | 29.6312 | 69.3257 | 37.4722 | [7 empty] | l/s | W
[19 empty] | 6,5V | 85.2194 | 60.5778
5V | 59.2325 | 49.3754 | 25.4173 | A | B | C |  |  | 5V | 57.9216 | 62.2127 | 26.8644 |  | A | B | C |  |  |  | 75.3089 | 55.5276
| 52.5899 | 50.5479 | 24.3443 | -0.0046444 | 0.43795 | 39.9274 |  |  |  | 49.6872 | 62.5797 | 24.6106 |  | -0.0016762 | 0.12277 | 60.6891 |  |  |  | 42.1776 | 37.7649
| 42.6813 | 49.8364 | 21.0731 | [6 empty] | 33.798 | 62.9786 | 20.9894 | [7 empty] | 81.7942 | 61.6094
| 31.091 | 49.1418 | 18.0716 | [6 empty] | 21.2461 | 62.5206 | 17.3035 | [7 empty] | 68.9613 | 55.2532
[20 empty] | 46.5991 | 44.8711
3V | 31.7062 | 38.5742 | 7.6543 | A | B | C |  |  | 3V | 28.2613 | 50.3046 | 7.4177 |  | A | B | C |  |  |  | 29.6312 | 37.4722
| 26.8268 | 39.3507 | 7.0952 | -0.011004 | 0.6276 | 29.9248 |  |  |  | 23.704 | 50.9103 | 6.912 |  | -0.010956 | 0.46497 | 45.9536 |  |  |  | l/s | W
| 21.2246 | 37.7928 | 6.4091 | [6 empty] | 16.9931 | 50.6099 | 6.4397 | [6 empty] | 5V | 59.2325 | 25.4173
| 16.0877 | 37.3467 | 6.0005 | [6 empty] | 11.4648 | 49.8743 | 6.1312 | [7 empty] | 52.5899 | 24.3443
[20 empty] | 31.091 | 18.0716
[20 empty] | 57.9216 | 26.8644
[20 empty] | 49.6872 | 24.6106
[20 empty] | 33.798 | 20.9894
[20 empty] | 21.2461 | 17.3035
[20 empty] | l/s | W
[19 empty] | 3V | 31.7062 | 7.6543
[20 empty] | 26.8268 | 7.0952
[20 empty] | 21.2246 | 6.4091
[20 empty] | 28.2613 | 7.4177
[20 empty] | 23.704 | 6.912
[20 empty] | 16.9931 | 6.4397
[20 empty] | 11.4648 | 6.1312

## Laskenta vaipan läpi 100 (hidden)
Ohjausjännite
Tulo | 4.9821 | V
Poisto | 4.6522 | V
Sovite ohj. Jännite vs. LwA vaipan läpi
y = LwA, x = ohjausjännite
y = Ax + B
| A | B
7,5 V - 10 V | 7.6565 | 31.9288
4 V - 7,5 V | 26.3292 | -5.5042
Maksimi | 4.9821 | V | ---> | 36.7767 | dB
Painotettu keskiarvo | 4.8722 | V | ---> | 36.1891 | dB
Korjaus
Äänitehotasot kanaviin
Imupuoli | Ulko | 45.3929 | dB
| Poisto | 46.4915 | dB
| Erotus | 1.0986 | dB
Painepuoli | Tulo | 60.2158 | dB
| Jäte | 60.7853 | dB
| Erotus | 0.56953 | dB
Keskiarvo erotus | 0.83409 | dB
Korjaus K | 4.5761 | dB
Taustamelukorjattu | 41.3528 | dB
Maksimikorjaus | 34.1767 | dB
|  |  |  | LpA10m2 | LpA2,5m2
Valinta | 36.1891 | dB |  | 32.2097 | 38.2303
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 15 | 10 | 5 | -5 | -14 | -20 | -26 | -30 | ---> | 51.1891 | 46.1891 | 41.1891 | 31.1891 | 22.1891 | 16.1891 | 10.1891 | 6.1891 | 52.7361 | 36.0395 | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta tulopuoli 150 (hidden)
Tuloilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste
[7 empty] | 25 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [12 empty] | A | B | [9 empty] | 10 V |  | 6,5 V |  | 5 V |  | 3 V
x = til.virta | [11 empty] | 5-10V | 15.0445 | -4.581 | Ulko | 43.8455 | dB | ---> | Ulko | 42.7211 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 3-6,5V | 23.3306 | -32.3771 | Ulko | 42.7211 | dB | [6 empty] | 60 | 163.2762 | 40 | 119.6113 | 25 | 85.8715 | 10 | 45.1029
2. aste polynomi | [23 empty] | 120 | 155.0178 | 50 | 117.5442 | 40 | 82.3209 | 20 | 41.7736
A | B | C | [9 empty] | 5-10V | 32.638 | -62.0527 | Tulo | 43.005 | dB | ----> | Tulo | 44.3724 | dB |  |  | 190 | 145.3723 | 100 | 107.5157 | 60 | 77.6141 | 25 | 40.0439
-0.00045001 | -7.1221 | 1234.8647 | [9 empty] | 3-5V | 27.3576 | -43.6882 | Tulo | 44.3724 | dB | [6 empty] | 250 | 137.0955 | 150 | 97.9473 | 80 | 72.9382 | 30 | 38.2659
[19 empty] | Max qV | 180 |  |  |  | 320 | 127.4285 | 170 | 94.2353 | 100 | 68.2925 | 50 | 30.5755
6,5V | [12 empty] | Sovite ohjausjännitteelle | [5 empty] | Max paine 10V | 600 | Pa |  |  | 350 | 123.282 | 190 | 90.5844 | 130 | 61.3793
2. aste polynomi | [12 empty] | 0-6,5 | 0 | 0.1151 | 0.58484 |  | ---> | Tulopuhallin | 3.4623 | V | OK |  | 420 | 113.5983 | 240 | 81.7056
A | B | C | [10 empty] | 6,5 - 10V | 0 | 0.20846 | -4.2371 |  |  |  | FALSE
0.012234 | -7.7391 | 790.6597 | [10 empty] | Valinta | 0 | 0.1151 | 0.58484 |  |  | Minimi-ilmavirta | 30 | l/s | Pulkkasen maili 18.6.19
[19 empty] | Max | 169 | W
5V | [17 empty] | ----> | Tulopuhallin | 13.883 | W
2. aste polynomi | [12 empty] | Polynomisovite teholle | [5 empty] | Rajoitus | 13.883 | W
A | B | C | [10 empty] | 0.075487 | -3.5379 | 55.1511
0.0029851 | -4.7266 | 408.8709 | [16 empty] | Poistopuhallin | 15.2242
[19 empty] | Elektroniikka | 3
3V
2. aste polynomi | [18 empty] | Total power | 32.1072 | W
A | B | C | [16 empty] | Maks qV | 26.9444 | l/s
-0.022344 | -1.0624 | 103.3734 | [16 empty] | SFP | 1.1916 | kW/m3/s
Verkkokäyrän potenssikäyrän termi
alfa
0.16
[18 empty] | Verkkokäyrä mitoituspisteelle | [16 empty] | Tehostusvara
[18 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite
[18 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella |  |  |  | Sovite ohjausjännitteelle, tehostuspistes
[18 empty] | 10 | -0.00045001 | -7.1221 | 1234.8647 | -0.16045 | -112.6863 | 68.2981 | 163.2762 | 68.2981 | 746.3405 | 166.5001 | 54.0672 | 78.1046 |  | 10 | 68.2981 |  | 173.2% |  |  | TRUE | (OK, jos TOSI) |  |  | 0 | 0.1151 | 0.58484
[18 empty] | 6.5 | 0.012234 | -7.7391 | 790.6597 | -0.14777 | -103.8821 | 51.5079 | 119.6113 | 51.5079 | 424.4903 | 70.1695 | 64.2228 | 62.1392 |  | 6.5 | 51.5079 |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[18 empty] | 5 | 0.0029851 | -4.7266 | 408.8709 | -0.15701 | -68.2547 | 38.1516 | 85.8715 | 38.1516 | 232.8874 | 33.0497 | 45.6007 | 58.961 |  | 5.75 | 44.8298 |  | 27.5 | l/s |  | 3.7501 | V
[18 empty] | 3 | -0.022344 | -1.0624 | 103.3734 | -0.18234 | -26.9008 | 21.0742 | 45.1029 | 21.0742 | 71.0598 | 13.2775 | 41.0808 | 38.6831 |  | 5 | 38.1516 |  | 121 | Pa
[32 empty] | 4 | 29.6129
[18 empty] | Spektrikorjaukset |  | Lwokt = LwA + K | [11 empty] | 3 | 21.0742
[20 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  |  |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[18 empty] | Ulkokanava |  | 17.3503 | 10.6308 | 5.0989 | -4.4664 | -18.9881 | -23.7384 | -30 | -35 |  |  | ---> | 61.1958 | 54.4763 | 48.9445 | 39.3791 | 24.8574 | 20.1071 | 13.8455 | 8.8455 | 62.2656 | 44.064 | Tarkista laskenta!
[18 empty] | Tulokanava |  | 11.0846 | 10.1261 | 5.509 | -4.3228 | -13.3857 | -13.8143 | -23.9333 | -28.759 |  |  | ----> | 55.4569 | 54.4985 | 49.8814 | 40.0495 | 30.9867 | 30.558 | 20.4391 | 15.6134 | 58.71 | 44.617 | OK
Ohj-jännite lähin
[18 empty] | Ulkokanava | 10 | 15.2959 | 6.9607 | 1.9355 | 0.80413 | -13.483 | -17.3567 | -22.4696 | -29.6855 | 6.5377 |  |  | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
[19 empty] | 6.5 | 14.1369 | 5.8347 | 3.3756 | 1.0257 | -16.7323 | -20.9218 | -26.6338 | -32.1788 | 3.0377
[19 empty] | 5 | 13.2073 | 7.2733 | 6.0198 | -5.5138 | -18.7249 | -22.9829 | -29.2356 | -33 | 1.5377
[19 empty] | 3 | 17.3503 | 10.6308 | 5.0989 | -4.4664 | -18.9881 | -23.7384 | -30 | -35 | 0.46235
[18 empty] | VALINTA | 4 | 17.3503 | 10.6308 | 5.0989 | -4.4664 | -18.9881 | -23.7384 | -30 | -35 | 0.46235
Ohj-jännite lähin
[18 empty] | Tulokanava | 10 | 9.0861 | 4.616 | 0.01421 | -0.99376 | -8.5773 | -8.3183 | -12.1571 | -16.1042 | 6.5377
[19 empty] | 6.5 | 8.3586 | 4.1895 | 1.1897 | 1.3114 | -10.8028 | -10.7671 | -15.524 | -19.7586 | 3.0377
[19 empty] | 5 | 9.0199 | 5.3967 | 5.3186 | -4.0658 | -11.1186 | -11.2556 | -17.0528 | -23.3697 | 1.5377
[19 empty] | 3 | 11.0846 | 10.1261 | 5.509 | -4.3228 | -13.3857 | -13.8143 | -23.9333 | -28.759 | 0.46235
[18 empty] | VALINTA | 4 | 11.0846 | 10.1261 | 5.509 | -4.3228 | -13.3857 | -13.8143 | -23.9333 | -28.759 | 0.46235
Mitatut pisteet
Ulkokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Tulokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | RPM | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P | RPM | 3. aste polynomisovitus | [5 empty] | l/s | W
10V | 157.2831 | 59.5841 | 166.4811 | 4020 | A | B |  |  |  | 10V | 157.1239 | 73.5863 | 168.369 | 4020 | A | B | C |  |  | 10V | 157.2831 | 166.4811
| 146.5508 | 59.0347 | 166.4292 | 4006.6667 | -0.00024254 | 0.11644 | 47.2457 |  |  |  | 146.4038 | 72.5986 | 168.1432 | 4006.6667 | 0.0020152 | -0.50466 | 103.1716 |  |  |  | 146.5508 | 166.4292
| 135.1697 | 58.6165 | 166.5273 | 3993.3333 | [6 empty] | 134.6249 | 71.6435 | 168.2705 | 4013.3333 | [6 empty] | 135.1697 | 166.5273
| 122.8739 | 57.8724 | 166.3235 | 4020 | [6 empty] | 122.8132 | 71.6247 | 168.0924 | 4026.6667 | [6 empty] | 122.8739 | 166.3235
[21 empty] | 157.1239 | 168.369
6,5V | 115.7956 | 56.1973 | 80.6081 | 3120 | A | B |  |  |  | 6,5V | 115.7527 | 69.4104 | 81.5241 | 3113.3333 | A | B | C |  |  |  | 146.4038 | 168.1432
| 106.9768 | 55.2374 | 80.6942 | 3113.3333 | 0.0043868 | -0.85842 | 96.7999 |  |  |  | 106.9167 | 68.2738 | 81.53 | 3120 | -0.00055969 | 0.20509 | 53.0601 |  |  |  | 134.6249 | 168.2705
| 98.2066 | 54.7415 | 79.1652 | 3113.3333 | [6 empty] | 97.6684 | 68.0622 | 80.0716 | 3080 | [6 empty] | 122.8132 | 168.0924
| 88.918 | 55.175 | 78.9036 | 3100 | [6 empty] | 88.4712 | 66.7212 | 79.7313 | 3120 | [6 empty] | l/s | W
[20 empty] | 6,5V | 115.7956 | 80.6081
5V | 84.3573 | 51.3969 | 39.2639 | 2400 | A | B | C |  |  | 5V | 84.2761 | 62.2216 | 39.7084 | 2393.3333 | A | B | C |  |  |  | 106.9768 | 80.6942
| 78.5038 | 50.6872 | 39.2051 | 2400 | -0.0013756 | 0.29222 | 36.4543 |  |  |  | 78.3667 | 61.7698 | 39.6124 | 2386.6667 | -0.00027736 | 0.10406 | 55.3948 |  |  |  | 88.918 | 78.9036
| 72.3832 | 50.6125 | 39.1155 | 2400 | [6 empty] | 71.9435 | 61.5184 | 39.565 | 2400 | [6 empty] | 115.7527 | 81.5241
| 65.6007 | 49.6395 | 38.5673 | 2400 | [6 empty] | 65.4929 | 60.9962 | 38.9735 | 2400 | [6 empty] | 106.9167 | 81.53
[21 empty] | 97.6684 | 80.0716
3V | 45.0437 | 38.8579 | 12.3406 | 1440 | A | B | C |  |  | 3V | 45.0563 | 51.1722 | 12.4796 | 1473.3333 | A | B | C |  |  |  | 88.4712 | 79.7313
| 42.8672 | 38.772 | 12.1707 | 1440 | 0.010045 | -0.75459 | 52.5217 |  |  |  | 42.8359 | 51.491 | 12.2977 | 1480 | -0.027284 | 2.327 | 1.7604 |  |  |  | l/s | W
| 40.2009 | 38.3121 | 12.0681 | 1480 | [6 empty] | 40.0468 | 51.1019 | 12.2065 | 1440 | [5 empty] | 5V | 84.3573 | 39.2639
| 36.7016 | 38.3859 | 11.9368 | 1466.6667 | [6 empty] | 36.6104 | 50.4087 | 12.0626 | 1440 | [6 empty] | 78.5038 | 39.2051
[21 empty] | 65.6007 | 38.5673
[21 empty] | 84.2761 | 39.7084
[21 empty] | 78.3667 | 39.6124
[21 empty] | 71.9435 | 39.565 |  | Tehon sovitteet 2. aste polynomi
[21 empty] | 65.4929 | 38.9735 |  |  | A | B | C
[21 empty] | l/s | W |  | 10V | -0.00010756 | 0.0342 | 164.666
[20 empty] | 3V | 45.0437 | 12.3406 |  | 6,5V | -0.0027577 | 0.63167 | 44.95
[21 empty] | 42.8672 | 12.1707 |  | 5V | -0.0038308 | 0.60756 | 15.4462
[21 empty] | 40.2009 | 12.0681 |  | 3V | 0.004883 | -0.35935 | 18.6819
[21 empty] | 45.0563 | 12.4796
[21 empty] | 42.8359 | 12.2977
[21 empty] | 40.0468 | 12.2065
[21 empty] | 36.6104 | 12.0626
[20 empty] | 15.2959 | 6.9607 | 1.9355 | 0.80413 | -13.483 | -17.3567 | -22.4696 | -29.6855
[20 empty] | 14.1369 | 5.8347 | 3.3756 | 1.0257 | -16.7323 | -20.9218 | -26.6338 | -32.1788
[20 empty] | 13.2073 | 7.2733 | 6.0198 | -5.5138 | -18.7249 | -22.9829 | -29.2356 | -33
[20 empty] | 17.3503 | 10.6308 | 5.0989 | -4.4664 | -18.9881 | -23.7384 | -30 | -35

## Laskenta poistopuoli 150 (hidden)
Poistoilma tilavuusvirta vs. painehäviö | [6 empty] | Syötä piste
[7 empty] | 26.9444 | l/s | 100 | Pa |  |  | Logaritmisovite LwA vs qV | [10 empty] | Pisteitä käyrien piirtämistä varten
y = paine | [12 empty] | A | B | [9 empty] | 10 V |  | 6,5 V |  | 5 V |  | 3 V
x = til.virta | [11 empty] | 5-10V | 3.5727 | 36.0629 | Ulko | 47.8308 | dB | ---> | Poisto | 43.392 | dB |  |  | Pa | l/s | Pa | l/s | Pa | l/s | Pa | l/s
10V | [11 empty] | 3-6,5V | 11.9329 | 4.0878 | Ulko | 43.392 | dB | [6 empty] | 100 | 179.1169 | 50 | 131.1425 | 35 | 96.2168 | 15 | 52.3549
2. aste polynomi | [23 empty] | 120 | 174.8986 | 50 | 131.1425 | 40 | 94.7293 | 20 | 50.4926
A | B | C | [9 empty] | 5-10V | 8.9754 | 30.5869 | Tulo | 60.1497 | dB | ----> | Jäte | 51.3092 | dB |  |  | 190 | 162.276 | 100 | 119.3542 | 60 | 88.8966 | 25 | 48.58
0.047761 | -21.6495 | 2445.4675 | [9 empty] | 3-5V | 27.1389 | -38.0804 | Tulo | 51.3092 | dB | [6 empty] | 250 | 153.1626 | 150 | 107.9338 | 80 | 83.2391 | 30 | 46.6127
[19 empty] | Max qV | 200 |  |  |  | 320 | 143.7877 | 170 | 103.4612 | 100 | 77.7419 | 55 | 35.749
6,5V | [12 empty] | Sovite ohjausjännitteelle | [5 empty] | Max pain 10V | 750 | Pa | OK |  | 390 | 135.3707 | 190 | 99.0404 | 138 | 67.694
2. aste polynomi | [12 empty] | 0-6,5 | 0 | 0.11418 | 0.26507 |  | ---> | Poistopuhallin | 3.3416 | V |  |  | 450 | 128.7304 | 235 | 89.274
A | B | C | [10 empty] | 6,5 - 10V | 0 | 0.11856 | 0.06676 |  |  |  | FALSE
0.0058882 | -5.7165 | 698.4022 | [10 empty] | Valinta | 0 | 0.11418 | 0.26507 |  |  | Minimi-ilmavirta | 30 | l/s | Pulkkasen maili 18.6.19
[19 empty] | Max | 169 | W
5V | [17 empty] | ----> | Poistopuhallin | 11.8371 | W
2. aste polynomi | [12 empty] | Polynomisovite teholle | [5 empty] | Rajoitus | 11.8371 | W
A | B | C | [10 empty] | 0.029734 | -0.48407 | 3.2934
0.0092418 | -5.126 | 442.6477
3V
2. aste polynomi
A | B | C
-0.01873 | -0.75858 | 106.0555
Verkkokäyrän potenssikäyrän termi
alfa
0.13774
[18 empty] | Verkkokäyrä mitoituspisteelle | [16 empty] | Tehostusvara
[18 empty] | Ohjaus | Sovitteen parametrit |  |  |  | Leikkauskohdat |  |  | Valinta |  | Teho | LwA |  |  | Ohjausjännite
[18 empty] | V | A | B | C | A' = A-alfa | Leik. 1 | Leik. 2 | Max | l/s | Pa | P | Ulko | Tulo |  | V | l/s |  | Maksimi tehostusvara |  |  | Tarkistus onko käyttöalueella |  |  |  | Sovite ohjausjännitteelle, tehostuspistes
[18 empty] | 10 | 0.047761 | -21.6495 | 2445.4675 | -0.089979 | -324.3878 | 83.7828 | 179.1169 | 83.7828 | 966.8776 | 170.3204 | 51.2831 | 68.1354 |  | 10 | 83.7828 |  | 210.9% |  |  | TRUE | (OK, jos TOSI) |  |  | 0 | 0.11418 | 0.26507
[18 empty] | 6.5 | 0.0058882 | -5.7165 | 698.4022 | -0.13185 | -97.6167 | 54.2618 | 131.1425 | 54.2618 | 405.5544 | 72.1852 | 51.9556 | 72.3691 |  | 6.5 | 54.2618 |  | Haluttu tehostuspiste |  |  | Tehostuspisteen ohjausjännite
[18 empty] | 5 | 0.0092418 | -5.126 | 442.6477 | -0.1285 | -81.9343 | 42.043 | 96.2168 | 42.043 | 243.4721 | 26.5241 | 48.3974 | 60.4032 |  | 5.75 | 48.1524 |  | 29.6389 | l/s |  | 3.6492 | V
[18 empty] | 3 | -0.01873 | -0.75858 | 106.0555 | -0.15647 | -28.5712 | 23.7231 | 52.3549 | 23.7231 | 77.5184 | 11.039 | 41.9663 | 48.7728 |  | 5 | 42.043 |  | 121 | Pa
[32 empty] | 4 | 32.8831
[18 empty] | Spektrikorjaukset |  | Lwokt = LwA + K | [11 empty] | 3 | 23.7231
[20 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  |  |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
[18 empty] | Poistokanava |  | 11.3094 | 11.1129 | 6.4459 | -8.112 | -18.6898 | -25.1055 | -30 | -34 |  |  | ---> | 59.1402 | 58.9437 | 54.2767 | 39.7188 | 29.141 | 22.7252 | 17.8308 | 13.8308 | 62.7477 | 48.0495 | Tarkista laskenta!
[18 empty] | Jätekanava |  | 8.1746 | 7.9779 | 7.0101 | -4.1122 | -14.1003 | -15.0481 | -24.4989 | -30.3534 |  |  | ----> | 59.4838 | 59.2871 | 58.3193 | 47.197 | 37.2089 | 36.2612 | 26.8103 | 20.9558 | 63.9413 | 51.8565 | Tarkista laskenta!
Ohj-jännite lähin
[18 empty] | Poistokanava | 10 | 16.6438 | 9.6039 | 3.4633 | -0.90276 | -11.0444 | -14.7687 | -20.8018 | -28.4571 | 6.6584 |  |  | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1
[19 empty] | 6.5 | 19.3786 | 8.4557 | 3.4065 | -1.0894 | -12.9526 | -17.8548 | -24.3427 | -30.8413 | 3.1584
[19 empty] | 5 | 12.1063 | 8.8717 | 6.5499 | -6.3233 | -15.0656 | -20.5696 | -27.7957 | -32 | 1.6584
[19 empty] | 3 | 11.3094 | 11.1129 | 6.4459 | -8.112 | -18.6898 | -25.1055 | -30 | -34 | 0.34159
[18 empty] | VALINTA | 4 | 11.3094 | 11.1129 | 6.4459 | -8.112 | -18.6898 | -25.1055 | -30 | -34 | 0.34159
Ohj-jännite lähin
[18 empty] | Jätekanava | 10 | 9.2947 | 3.058 | -0.058582 | 0.19913 | -9.9786 | -9.0529 | -12.7987 | -17.82 | 6.6584
[19 empty] | 6.5 | 7.3234 | 1.4452 | 2.588 | 1.054 | -12.2853 | -11.6585 | -16.3036 | -22.1867 | 3.1584
[19 empty] | 5 | 6.7221 | 2.7302 | 5.8797 | -3.8772 | -12.3491 | -12.1147 | -17.7795 | -26.2873 | 1.6584
[19 empty] | 3 | 8.1746 | 7.9779 | 7.0101 | -4.1122 | -14.1003 | -15.0481 | -24.4989 | -30.3534 | 0.34159
[18 empty] | VALINTA | 4 | 8.1746 | 7.9779 | 7.0101 | -4.1122 | -14.1003 | -15.0481 | -24.4989 | -30.3534 | 0.34159
Mitatut pisteet
Poistokanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Jätekanava |  |  |  |  | Äänisovitteet tilavuusvirralle |  |  |  |  | Teho vs tilavuusvirta
| l/s | LwA | P | RPM | Sovitteet 2. ja 3. aste riippuen tilanteesta | [5 empty] | l/s | LwA | P | RPM | 3. aste polynomisovitus | [5 empty] | l/s | W
10V | 177.3731 | 59.0606 | 168.5426 | 4086.6667 | A | B |  |  |  | 10V | 177.7357 | 75.3344 | 166.1277 | 4066.6667 | A | B | C |  |  | 10V | 177.3731 | 168.5426
| 163.079 | 58.4876 | 167.5994 | 4060 | -0.00094551 | 0.32887 | 30.3666 |  |  |  | 163.4999 | 74.7238 | 166.438 | 4020 | -0.00042303 | 0.18725 | 55.4163 |  |  |  | 163.079 | 167.5994
| 150.0525 | 58.851 | 169.1781 | 4053.3333 | [6 empty] | 150.9372 | 74.0422 | 167.0423 | 4006.6667 | [6 empty] | 150.0525 | 169.1781
| 139.4561 | 57.672 | 169.169 | 4040 | [6 empty] | 139.8137 | 73.3276 | 166.2714 | 4013.3333 | [6 empty] | 139.4561 | 169.169
[21 empty] | 177.7357 | 166.1277
6,5V | 128.9069 | 54.4515 | 74.8204 | 3073.3333 | A | B |  |  |  | 6,5V | 129.1999 | 71.0153 | 74.6647 | 3080 | A | B | C |  |  |  | 163.4999 | 166.438
| 118.9205 | 54.0671 | 75.8333 | 3060 | -0.00083589 | 0.1844 | 44.4107 |  |  |  | 118.4938 | 69.2074 | 75.607 | 3066.6667 | 0.0018677 | -0.36322 | 86.5791 |  |  |  | 150.9372 | 167.0423
| 108.0924 | 55.0179 | 75.1297 | 3053.3333 | [6 empty] | 107.7379 | 69.6675 | 75.0085 | 3053.3333 | [6 empty] | 139.8137 | 166.2714
| 97.6377 | 54.2973 | 75.0299 | 3060 | [6 empty] | 96.4564 | 68.7474 | 76.1477 | 3073.3333 | [6 empty] | l/s | W
[20 empty] | 6,5V | 128.9069 | 74.8204
5V | 96.446 | 50.7052 | 37.5216 | 2366.6667 |  | A | B |  |  | 5V | 96.6772 | 63.4747 | 37.6715 | 2358 | A | B | C |  |  |  | 118.9205 | 75.8333
| 89.483 | 49.8622 | 38.0302 | 2366.6667 |  | 0.037361 | 46.8266 |  |  |  | 89.05 | 63.1211 | 38.1314 | 2360 | -0.00049836 | 0.12485 | 56.0349 |  |  |  | 97.6377 | 75.0299
| 81.9133 | 49.6905 | 37.6053 | 2346.6667 | [6 empty] | 81.1134 | 62.9641 | 38.1113 | 2373.3333 | [6 empty] | 129.1999 | 74.6647
| 74.6051 | 49.8427 | 37.5534 | 2346.6667 | [6 empty] | 73.6625 | 62.4994 | 37.0312 | 2352 | [6 empty] | 118.4938 | 75.607
[21 empty] | 107.7379 | 75.0085
3V | 52.6915 | 41.3801 | 12.146 | 1433.3333 |  | A | B |  |  | 3V | 52.6744 | 52.4599 | 12.164 | 1446.6667 | A | B | C |  |  |  | 96.4564 | 76.1477
| 50.6337 | 41.6071 | 12.0559 | 1433.3333 |  | -0.013616 | 42.2893 |  |  |  | 50.3141 | 51.839 | 12.0189 | 1440 | 0.000637 | 0.075666 | 46.6193 |  |  |  | l/s | W
| 47.4255 | 42.1123 | 12.1281 | 1433.3333 | [6 empty] | 47.0621 | 51.7428 | 12.0573 | 1433.3333 | [5 empty] | 5V | 96.446 | 37.5216
| 43.9553 | 41.4065 | 12.0878 | 1440 | [6 empty] | 43.0176 | 51.0137 | 11.9241 | 1433.3333 | [6 empty] | 89.483 | 38.0302
[21 empty] | 74.6051 | 37.5534
[21 empty] | 96.6772 | 37.6715
[21 empty] | 89.05 | 38.1314
[21 empty] | 81.1134 | 38.1113 |  | Tehon sovitteet 2. aste polynomi
[21 empty] | 73.6625 | 37.0312 |  |  | A | B | C
[21 empty] | l/s | W |  | 10V | 0.00025026 | -0.098635 | 176.8277
[20 empty] | 3V | 52.6915 | 12.146 |  | 6,5V | -0.0013105 | 0.27612 | 61.0608
[21 empty] | 50.6337 | 12.0559 |  | 5V | -0.0059349 | 1.0253 | -6.0914
[21 empty] | 47.4255 | 12.1281 |  | 3V | -0.00097182 | 0.11181 | 8.9334
[21 empty] | 52.6744 | 12.164
[21 empty] | 50.3141 | 12.0189
[21 empty] | 47.0621 | 12.0573
[21 empty] | 43.0176 | 11.9241

## Laskenta vaipan läpi 150 (hidden)
Ohjausjännite
Tulo | 4.621 | V
Poisto | 4.3915 | V
Sovite ohj. Jännite vs. LwA vaipan läpi
y = LwA, x = ohjausjännite
y = Ax + B
| A | B
Kaikki voltit | 12.2903 | 19.608
Maksimi | 4.621 | V | ---> | 38.4196 | dB
Painotettu keskiarvo | 4.5445 | V | ---> | 38.2145 | dB
Korjaus
Äänitehotasot kanaviin
Imupuoli | Ulko | 45.3929 | dB
| Poisto | 46.4915 | dB
| Erotus | 1.0986 | dB
Painepuoli | Tulo | 60.2158 | dB
| Jäte | 60.7853 | dB
| Erotus | 0.56953 | dB
Keskiarvo erotus | 0.83409 | dB
Korjaus K | 4.5761 | dB
Taustamelukorjattu | 42.9957 | dB
Maksimikorjaus | 35.8196 | dB
|  |  |  | LpA10m2 | LpA2,5m2
Valinta | 38.2145 | dB |  | 34.2351 | 40.2557
Spektrikorjaukset | Lwokt = LwA + K
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 |  | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lwtot | LwAtot
Vaipan läpi | 11 | 6 | 6 | -4 | -16 | -18 | -23 | -24 | ---> | 49.2145 | 44.2145 | 44.2145 | 34.2145 | 22.2145 | 20.2145 | 15.2145 | 14.2145 | 51.4366 | 37.8685 | OK
[10 empty] | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## SäädataC (hidden)
| Kielivalinta | Aloitus | Määrä
FALSE | Suomi | 0 | 4 |  | Suomi, TRY 2020 | [16 empty] | Valinta
TRUE | Muut | 4 | 13 |  | I (Vantaa) | II (Jokioinen) | III (Jyväskylä) | IV (Sodankylä) | SWE - Stockholm | SWE - Gothenburg | EST - Tallinn | LAT - Riga | LTU - Vilnius | POL - Warsaw | POL - Krakow | POL - Gdansk | ISL - Reykjavík | ROU - Bucharest | NOR - Oslo | DEN - Copenhagen | GER - Berlin | SWE - Stockholm | I (Vantaa) | II (Jokioinen) | III (Jyväskylä) | IV (Sodankylä) | EST - Tallinn | NOR - Oslo | DEN - Copenhagen | POL - Warsaw | GER - Berlin | ISL - Reykjavík | RO - Bucharest | LAT - Riga | LTU - Vilnius | POL - Gdansk | POL - Krakow | SWE - Stockholm | SWE - Gothenburg
| Valinta | 4 | 13 | -40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tallinna | Oslo | Köpis | Varsova | Berliini | Reyk | Buka | Riika | Vilna | Gdansk | Krakova | Stökis | Goteb
|  |  |  | -39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Otsikot |  |  |  | -38 | 0 | 0 | 0 | 0.00034247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I (Vantaa) |  | SWE - Stockholm |  | -37 | 0 | 0 | 0 | 0.00057078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00057078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
II (Jokioinen) |  | SWE - Gothenburg |  | -36 | 0 | 0 | 0 | 0.0011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0
III (Jyväskylä) |  | EST - Tallinn |  | -35 | 0 | 0 | 0 | 0.0018265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018265 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IV (Sodankylä) |  | LAT - Riga |  | -34 | 0 | 0 | 0 | 0.002968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002968 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWE - Stockholm |  | LTU - Vilnius |  | -33 | 0 | 0 | 0 | 0.0041096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041096 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWE - Gothenburg |  | POL - Warsaw |  | -32 | 0 | 0 | 0 | 0.0047945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047945 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EST - Tallinn |  | POL - Krakow |  | -31 | 0 | 0 | 0.00022831 | 0.0060502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00022831 | 0.0060502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAT - Riga |  | POL - Gdansk |  | -30 | 0 | 0 | 0.00034247 | 0.0079909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0.0079909 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LTU - Vilnius |  | ISL - Reykjavík |  | -29 | 0 | 0 | 0.00045662 | 0.011187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00045662 | 0.011187 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POL - Warsaw |  | ROU - Bucharest |  | -28 | 0 | 0 | 0.00091324 | 0.014726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00091324 | 0.014726 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POL - Krakow |  | NOR - Oslo |  | -27 | 0 | 0 | 0.0018265 | 0.019064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018265 | 0.019064 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POL - Gdansk |  | DEN - Copenhagen |  | -26 | 0 | 0.00034247 | 0.0026256 | 0.022489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0.0026256 | 0.022489 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISL - Reykjavík |  | GER - Berlin |  | -25 | 0 | 0.00091324 | 0.0038813 | 0.027397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00091324 | 0.0038813 | 0.027397 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ROU - Bucharest |  |  |  | -24 | 0.00011416 | 0.0013699 | 0.0058219 | 0.030936 | 0 | 0 | 0 | 0 | 0.00011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00011416 | 0.0013699 | 0.0058219 | 0.030936 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOR - Oslo |  |  |  | -23 | 0.00034247 | 0.0023973 | 0.0073059 | 0.034018 | 0 | 0 | 0 | 0 | 0.0011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0.0023973 | 0.0073059 | 0.034018 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEN - Copenhagen |  |  |  | -22 | 0.00057078 | 0.002968 | 0.0083333 | 0.041096 | 0 | 0 | 0 | 0 | 0.0022831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00057078 | 0.002968 | 0.0083333 | 0.041096 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GER - Berlin |  |  |  | -21 | 0.0011416 | 0.0045662 | 0.010616 | 0.048059 | 0 | 0 | 0 | 0 | 0.0033105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011416 | 0.0045662 | 0.010616 | 0.048059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | -20 | 0.0028539 | 0.0058219 | 0.012671 | 0.055251 | 0 | 0 | 0 | 0 | 0.0055936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028539 | 0.0058219 | 0.012671 | 0.055251 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | -19 | 0.0053653 | 0.0077626 | 0.016553 | 0.062557 | 0 | 0 | 0 | 0.00034247 | 0.0063927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0053653 | 0.0077626 | 0.016553 | 0.062557 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | -18 | 0.0070776 | 0.010046 | 0.01895 | 0.068037 | 0 | 0 | 0 | 0.0025114 | 0.0070776 | 0.00034247 | 0 | 0 | 0 | 0 | 0.00045662 | 0 | 0 | 0 | 0.0070776 | 0.010046 | 0.01895 | 0.068037 | 0 | 0.00045662 | 0 | 0.00034247 | 0 | 0 | 0
1 | Valittu alue listasta |  |  | -17 | 0.0092466 | 0.013128 | 0.023288 | 0.074543 | 0 | 0 | 0.00022831 | 0.003653 | 0.0079909 | 0.0010274 | 0.00011416 | 0 | 0 | 0 | 0.0018265 | 0 | 0 | 0 | 0.0092466 | 0.013128 | 0.023288 | 0.074543 | 0.00022831 | 0.0018265 | 0 | 0.0010274 | 0 | 0 | 0
1 | Tarkastus, jos on suurempi ollut kuin suomen |  |  | -16 | 0.011872 | 0.018265 | 0.028539 | 0.081621 | 0 | 0.00022831 | 0.0012557 | 0.0098174 | 0.011301 | 0.0020548 | 0.0018265 | 0 | 0 | 0 | 0.0037671 | 0 | 0 | 0 | 0.011872 | 0.018265 | 0.028539 | 0.081621 | 0.0012557 | 0.0037671 | 0 | 0.0020548 | 0 | 0 | 0
|  |  |  | -15 | 0.016324 | 0.023288 | 0.035845 | 0.090982 | 0 | 0.0021689 | 0.0047945 | 0.012443 | 0.01347 | 0.0037671 | 0.0034247 | 0 | 0 | 0 | 0.0063927 | 0 | 0.00011416 | 0 | 0.016324 | 0.023288 | 0.035845 | 0.090982 | 0.0047945 | 0.0063927 | 0 | 0.0037671 | 0.00011416 | 0 | 0
5 | Siirtymä säädatalistassa |  |  | -14 | 0.021918 | 0.029795 | 0.043493 | 0.10422 | 0 | 0.0025114 | 0.0068493 | 0.013927 | 0.015639 | 0.0047945 | 0.0044521 | 0 | 0 | 0 | 0.0074201 | 0 | 0.00068493 | 0 | 0.021918 | 0.029795 | 0.043493 | 0.10422 | 0.0068493 | 0.0074201 | 0 | 0.0047945 | 0.00068493 | 0 | 0
SWE - Stockholm | Otsikko |  |  | -13 | 0.028653 | 0.03653 | 0.051598 | 0.11747 | 0 | 0.0035388 | 0.012557 | 0.01621 | 0.020205 | 0.0067352 | 0.0075342 | 0 | 0 | 0.00068493 | 0.011301 | 0 | 0.0015982 | 0 | 0.028653 | 0.03653 | 0.051598 | 0.11747 | 0.012557 | 0.011301 | 0 | 0.0067352 | 0.0015982 | 0 | 0.00068493
|  |  |  | -12 | 0.034589 | 0.041324 | 0.060959 | 0.13345 | 0.00034247 | 0.0073059 | 0.019749 | 0.019863 | 0.028995 | 0.0097032 | 0.01016 | 0.00034247 | 0 | 0.0050228 | 0.014041 | 0 | 0.0037671 | 0.00034247 | 0.034589 | 0.041324 | 0.060959 | 0.13345 | 0.019749 | 0.014041 | 0 | 0.0097032 | 0.0037671 | 0 | 0.0050228
|  |  |  | -11 | 0.040639 | 0.048402 | 0.071575 | 0.15137 | 0.0013699 | 0.012671 | 0.029224 | 0.02911 | 0.036073 | 0.013356 | 0.013813 | 0.0013699 | 0.0012557 | 0.010274 | 0.018721 | 0 | 0.0054795 | 0.0013699 | 0.040639 | 0.048402 | 0.071575 | 0.15137 | 0.029224 | 0.018721 | 0 | 0.013356 | 0.0054795 | 0.0012557 | 0.010274
|  |  |  | -10 | 0.046575 | 0.056963 | 0.083105 | 0.16861 | 0.0049087 | 0.015753 | 0.040297 | 0.036416 | 0.04589 | 0.018037 | 0.016553 | 0.0049087 | 0.003653 | 0.013584 | 0.021233 | 0.0025114 | 0.008105 | 0.0049087 | 0.046575 | 0.056963 | 0.083105 | 0.16861 | 0.040297 | 0.021233 | 0.0025114 | 0.018037 | 0.008105 | 0.003653 | 0.013584
|  |  |  | -9 | 0.05468 | 0.067352 | 0.097945 | 0.1863 | 0.0067352 | 0.01758 | 0.048744 | 0.039498 | 0.052055 | 0.020548 | 0.018721 | 0.0067352 | 0.0047945 | 0.015068 | 0.023174 | 0.0030822 | 0.0092466 | 0.0067352 | 0.05468 | 0.067352 | 0.097945 | 0.1863 | 0.048744 | 0.023174 | 0.0030822 | 0.020548 | 0.0092466 | 0.0047945 | 0.015068
|  |  |  | -8 | 0.063356 | 0.076256 | 0.11667 | 0.20091 | 0.0091324 | 0.02363 | 0.062557 | 0.048402 | 0.067009 | 0.025228 | 0.025685 | 0.0091324 | 0.0090183 | 0.02032 | 0.030365 | 0.0050228 | 0.012785 | 0.0091324 | 0.063356 | 0.076256 | 0.11667 | 0.20091 | 0.062557 | 0.030365 | 0.0050228 | 0.025228 | 0.012785 | 0.0090183 | 0.02032
|  |  |  | -7 | 0.075 | 0.087785 | 0.13699 | 0.22237 | 0.011301 | 0.031849 | 0.084475 | 0.068379 | 0.082763 | 0.034018 | 0.038699 | 0.011301 | 0.013356 | 0.028311 | 0.039041 | 0.0086758 | 0.016553 | 0.011301 | 0.075 | 0.087785 | 0.13699 | 0.22237 | 0.084475 | 0.039041 | 0.0086758 | 0.034018 | 0.016553 | 0.013356 | 0.028311
|  |  |  | -6 | 0.08847 | 0.10217 | 0.16096 | 0.24121 | 0.023858 | 0.042808 | 0.10616 | 0.0879 | 0.10582 | 0.049087 | 0.054338 | 0.023858 | 0.022717 | 0.039954 | 0.053539 | 0.014041 | 0.021804 | 0.023858 | 0.08847 | 0.10217 | 0.16096 | 0.24121 | 0.10616 | 0.053539 | 0.014041 | 0.049087 | 0.021804 | 0.022717 | 0.039954
|  |  |  | -5 | 0.10548 | 0.12317 | 0.18801 | 0.2718 | 0.042922 | 0.059018 | 0.13071 | 0.11347 | 0.13071 | 0.069977 | 0.070205 | 0.042922 | 0.041895 | 0.053995 | 0.074543 | 0.020662 | 0.028767 | 0.042922 | 0.10548 | 0.12317 | 0.18801 | 0.2718 | 0.13071 | 0.074543 | 0.020662 | 0.069977 | 0.028767 | 0.041895 | 0.053995
|  |  |  | -4 | 0.12888 | 0.14452 | 0.21393 | 0.30651 | 0.056849 | 0.07032 | 0.14772 | 0.12911 | 0.14874 | 0.083447 | 0.081735 | 0.056849 | 0.049429 | 0.063699 | 0.086872 | 0.028767 | 0.03516 | 0.056849 | 0.12888 | 0.14452 | 0.21393 | 0.30651 | 0.14772 | 0.086872 | 0.028767 | 0.083447 | 0.03516 | 0.049429 | 0.063699
|  |  |  | -3 | 0.15571 | 0.16849 | 0.24406 | 0.34178 | 0.080936 | 0.10148 | 0.1734 | 0.16598 | 0.19075 | 0.1153 | 0.10251 | 0.080936 | 0.078539 | 0.084932 | 0.11781 | 0.044292 | 0.048858 | 0.080936 | 0.15571 | 0.16849 | 0.24406 | 0.34178 | 0.1734 | 0.11781 | 0.044292 | 0.1153 | 0.048858 | 0.078539 | 0.084932
|  |  |  | -2 | 0.18425 | 0.19338 | 0.27728 | 0.37648 | 0.11107 | 0.13516 | 0.20468 | 0.20228 | 0.22911 | 0.15377 | 0.1339 | 0.11107 | 0.11724 | 0.11016 | 0.16244 | 0.071689 | 0.066324 | 0.11107 | 0.18425 | 0.19338 | 0.27728 | 0.37648 | 0.20468 | 0.16244 | 0.071689 | 0.15377 | 0.066324 | 0.11724 | 0.11016
|  |  |  | -1 | 0.20925 | 0.2234 | 0.3121 | 0.41678 | 0.15719 | 0.16667 | 0.23185 | 0.24463 | 0.271 | 0.19121 | 0.16929 | 0.15719 | 0.15571 | 0.1347 | 0.21119 | 0.10148 | 0.10091 | 0.15719 | 0.20925 | 0.2234 | 0.3121 | 0.41678 | 0.23185 | 0.21119 | 0.10148 | 0.19121 | 0.10091 | 0.15571 | 0.1347
|  |  |  | 0 | 0.2492 | 0.27089 | 0.36792 | 0.46027 | 0.21256 | 0.20468 | 0.27363 | 0.28938 | 0.30811 | 0.22979 | 0.20833 | 0.21256 | 0.20274 | 0.16381 | 0.25753 | 0.14212 | 0.13904 | 0.21256 | 0.2492 | 0.27089 | 0.36792 | 0.46027 | 0.27363 | 0.25753 | 0.14212 | 0.22979 | 0.13904 | 0.20274 | 0.16381
|  |  |  | 1 | 0.30993 | 0.34224 | 0.41005 | 0.51119 | 0.24155 | 0.225 | 0.30491 | 0.3105 | 0.32968 | 0.24521 | 0.22888 | 0.24155 | 0.23379 | 0.18014 | 0.28151 | 0.1637 | 0.16233 | 0.24155 | 0.30993 | 0.34224 | 0.41005 | 0.51119 | 0.30491 | 0.28151 | 0.1637 | 0.24521 | 0.16233 | 0.23379 | 0.18014
|  |  |  | 2 | 0.36918 | 0.40137 | 0.45171 | 0.54372 | 0.30034 | 0.27112 | 0.36507 | 0.3524 | 0.36724 | 0.27717 | 0.2653 | 0.30034 | 0.29498 | 0.21107 | 0.3355 | 0.20742 | 0.19806 | 0.30034 | 0.36918 | 0.40137 | 0.45171 | 0.54372 | 0.36507 | 0.3355 | 0.20742 | 0.27717 | 0.19806 | 0.29498 | 0.21107
|  |  |  | 3 | 0.41598 | 0.44018 | 0.48653 | 0.57363 | 0.34852 | 0.32523 | 0.40559 | 0.39064 | 0.40274 | 0.31324 | 0.30445 | 0.34852 | 0.35856 | 0.24612 | 0.38824 | 0.26221 | 0.24201 | 0.34852 | 0.41598 | 0.44018 | 0.48653 | 0.57363 | 0.40559 | 0.38824 | 0.26221 | 0.31324 | 0.24201 | 0.35856 | 0.24612
|  |  |  | 4 | 0.4508 | 0.47717 | 0.51838 | 0.61016 | 0.40251 | 0.36781 | 0.45342 | 0.4266 | 0.43436 | 0.3476 | 0.33938 | 0.40251 | 0.41587 | 0.28128 | 0.44189 | 0.31358 | 0.29486 | 0.40251 | 0.4508 | 0.47717 | 0.51838 | 0.61016 | 0.45342 | 0.44189 | 0.31358 | 0.3476 | 0.29486 | 0.41587 | 0.28128
|  |  |  | 5 | 0.48413 | 0.50776 | 0.54886 | 0.63642 | 0.44121 | 0.41747 | 0.49874 | 0.46575 | 0.46701 | 0.38368 | 0.37614 | 0.44121 | 0.48139 | 0.3226 | 0.48162 | 0.36598 | 0.34167 | 0.44121 | 0.48413 | 0.50776 | 0.54886 | 0.63642 | 0.49874 | 0.48162 | 0.36598 | 0.38368 | 0.34167 | 0.48139 | 0.3226
|  |  |  | 6 | 0.51587 | 0.54167 | 0.58139 | 0.66416 | 0.46187 | 0.43938 | 0.5161 | 0.47979 | 0.48881 | 0.40742 | 0.39475 | 0.46187 | 0.51941 | 0.34121 | 0.49772 | 0.39087 | 0.36553 | 0.46187 | 0.51587 | 0.54167 | 0.58139 | 0.66416 | 0.5161 | 0.49772 | 0.39087 | 0.40742 | 0.36553 | 0.51941 | 0.34121
|  |  |  | 7 | 0.55331 | 0.58744 | 0.60719 | 0.69053 | 0.50445 | 0.48276 | 0.55011 | 0.51598 | 0.52466 | 0.44806 | 0.43379 | 0.50445 | 0.59178 | 0.36861 | 0.53231 | 0.44315 | 0.41495 | 0.50445 | 0.55331 | 0.58744 | 0.60719 | 0.69053 | 0.55011 | 0.53231 | 0.44315 | 0.44806 | 0.41495 | 0.59178 | 0.36861
|  |  |  | 8 | 0.58984 | 0.62123 | 0.63162 | 0.71872 | 0.54589 | 0.53139 | 0.58858 | 0.54749 | 0.55925 | 0.48413 | 0.47066 | 0.54589 | 0.66039 | 0.3992 | 0.56667 | 0.49167 | 0.45879 | 0.54589 | 0.58984 | 0.62123 | 0.63162 | 0.71872 | 0.58858 | 0.56667 | 0.49167 | 0.48413 | 0.45879 | 0.66039 | 0.3992
|  |  |  | 9 | 0.61747 | 0.654 | 0.66233 | 0.74886 | 0.58037 | 0.58151 | 0.62055 | 0.58288 | 0.59509 | 0.52466 | 0.50925 | 0.58037 | 0.73002 | 0.43333 | 0.60137 | 0.54167 | 0.50377 | 0.58037 | 0.61747 | 0.654 | 0.66233 | 0.74886 | 0.62055 | 0.60137 | 0.54167 | 0.52466 | 0.50377 | 0.73002 | 0.43333
|  |  |  | 10 | 0.64395 | 0.68836 | 0.69623 | 0.78527 | 0.6218 | 0.62409 | 0.65936 | 0.6258 | 0.63402 | 0.56393 | 0.55251 | 0.6218 | 0.79886 | 0.46849 | 0.64578 | 0.59041 | 0.54909 | 0.6218 | 0.64395 | 0.68836 | 0.69623 | 0.78527 | 0.65936 | 0.64578 | 0.59041 | 0.56393 | 0.54909 | 0.79886 | 0.46849
|  |  |  | 11 | 0.67626 | 0.72169 | 0.73105 | 0.82283 | 0.64635 | 0.64566 | 0.68094 | 0.6484 | 0.65228 | 0.58425 | 0.57043 | 0.64635 | 0.83482 | 0.48664 | 0.67169 | 0.6129 | 0.57066 | 0.64635 | 0.67626 | 0.72169 | 0.73105 | 0.82283 | 0.68094 | 0.67169 | 0.6129 | 0.58425 | 0.57066 | 0.83482 | 0.48664
|  |  |  | 12 | 0.71416 | 0.75297 | 0.76781 | 0.85114 | 0.69669 | 0.69372 | 0.71861 | 0.69326 | 0.6895 | 0.62785 | 0.60696 | 0.69669 | 0.89909 | 0.51895 | 0.72568 | 0.6589 | 0.61963 | 0.69669 | 0.71416 | 0.75297 | 0.76781 | 0.85114 | 0.71861 | 0.72568 | 0.6589 | 0.62785 | 0.61963 | 0.89909 | 0.51895
|  |  |  | 13 | 0.75434 | 0.78493 | 0.80594 | 0.87603 | 0.74589 | 0.74258 | 0.76404 | 0.7339 | 0.72397 | 0.66998 | 0.65228 | 0.74589 | 0.94418 | 0.55468 | 0.7758 | 0.70742 | 0.67043 | 0.74589 | 0.75434 | 0.78493 | 0.80594 | 0.87603 | 0.76404 | 0.7758 | 0.70742 | 0.66998 | 0.67043 | 0.94418 | 0.55468
|  |  |  | 14 | 0.78733 | 0.81975 | 0.84509 | 0.89578 | 0.79064 | 0.79098 | 0.80936 | 0.77215 | 0.75822 | 0.71792 | 0.69087 | 0.79064 | 0.97648 | 0.59064 | 0.82249 | 0.75582 | 0.72329 | 0.79064 | 0.78733 | 0.81975 | 0.84509 | 0.89578 | 0.80936 | 0.82249 | 0.75582 | 0.71792 | 0.72329 | 0.97648 | 0.59064
|  |  |  | 15 | 0.82626 | 0.85468 | 0.87568 | 0.91804 | 0.83756 | 0.83927 | 0.84532 | 0.81084 | 0.79429 | 0.7621 | 0.72911 | 0.83756 | 0.99235 | 0.63037 | 0.8613 | 0.79966 | 0.77203 | 0.83756 | 0.82626 | 0.85468 | 0.87568 | 0.91804 | 0.84532 | 0.8613 | 0.79966 | 0.7621 | 0.77203 | 0.99235 | 0.63037
|  |  |  | 16 | 0.86187 | 0.88059 | 0.89909 | 0.9355 | 0.86473 | 0.86073 | 0.86313 | 0.83116 | 0.81199 | 0.78048 | 0.75103 | 0.86473 | 0.99509 | 0.64772 | 0.88299 | 0.82386 | 0.79349 | 0.86473 | 0.86187 | 0.88059 | 0.89909 | 0.9355 | 0.86313 | 0.88299 | 0.82386 | 0.78048 | 0.79349 | 0.99509 | 0.64772
|  |  |  | 17 | 0.88995 | 0.90388 | 0.921 | 0.95274 | 0.90559 | 0.89224 | 0.8895 | 0.86906 | 0.85046 | 0.82352 | 0.79018 | 0.90559 | 0.9984 | 0.68196 | 0.91781 | 0.86336 | 0.83253 | 0.90559 | 0.88995 | 0.90388 | 0.921 | 0.95274 | 0.8895 | 0.91781 | 0.86336 | 0.82352 | 0.83253 | 0.9984 | 0.68196
|  |  |  | 18 | 0.91358 | 0.9226 | 0.93893 | 0.96712 | 0.93619 | 0.92683 | 0.91461 | 0.90148 | 0.8879 | 0.86461 | 0.82774 | 0.93619 | 1 | 0.71826 | 0.94509 | 0.89874 | 0.86906 | 0.93619 | 0.91358 | 0.9226 | 0.93893 | 0.96712 | 0.91461 | 0.94509 | 0.89874 | 0.86461 | 0.86906 | 1 | 0.71826
|  |  |  | 19 | 0.93219 | 0.93836 | 0.95491 | 0.97603 | 0.96176 | 0.94886 | 0.93642 | 0.92626 | 0.91838 | 0.89452 | 0.86473 | 0.96176 | 1 | 0.75205 | 0.9637 | 0.92626 | 0.9032 | 0.96176 | 0.93219 | 0.93836 | 0.95491 | 0.97603 | 0.93642 | 0.9637 | 0.92626 | 0.89452 | 0.9032 | 1 | 0.75205
|  |  |  | 20 | 0.94783 | 0.95491 | 0.96701 | 0.98265 | 0.97637 | 0.96632 | 0.954 | 0.9508 | 0.94201 | 0.92123 | 0.89692 | 0.97637 | 1 | 0.78436 | 0.9766 | 0.94806 | 0.92842 | 0.97637 | 0.94783 | 0.95491 | 0.96701 | 0.98265 | 0.954 | 0.9766 | 0.94806 | 0.92123 | 0.92842 | 1 | 0.78436
|  |  |  | 21 | 0.96324 | 0.96758 | 0.97808 | 0.9879 | 0.98345 | 0.97329 | 0.96107 | 0.96199 | 0.95126 | 0.93288 | 0.91256 | 0.98345 | 1 | 0.80137 | 0.98174 | 0.95913 | 0.93973 | 0.98345 | 0.96324 | 0.96758 | 0.97808 | 0.9879 | 0.96107 | 0.98174 | 0.95913 | 0.93288 | 0.93973 | 1 | 0.80137
|  |  |  | 22 | 0.97283 | 0.97751 | 0.98653 | 0.99167 | 0.99155 | 0.98436 | 0.97306 | 0.97409 | 0.96644 | 0.95091 | 0.93516 | 0.99155 | 1 | 0.83105 | 0.98847 | 0.97454 | 0.95685 | 0.99155 | 0.97283 | 0.97751 | 0.98653 | 0.99167 | 0.97306 | 0.98847 | 0.97454 | 0.95091 | 0.95685 | 1 | 0.83105
|  |  |  | 23 | 0.98082 | 0.98539 | 0.99304 | 0.99498 | 0.99692 | 0.99269 | 0.98265 | 0.98413 | 0.97785 | 0.96712 | 0.95525 | 0.99692 | 1 | 0.86107 | 0.99372 | 0.98562 | 0.96986 | 0.99692 | 0.98082 | 0.98539 | 0.99304 | 0.99498 | 0.98265 | 0.99372 | 0.98562 | 0.96712 | 0.96986 | 1 | 0.86107
|  |  |  | 24 | 0.9855 | 0.99098 | 0.9976 | 0.99749 | 0.99977 | 0.9976 | 0.99041 | 0.99132 | 0.98733 | 0.9782 | 0.97112 | 0.99977 | 1 | 0.8911 | 0.99635 | 0.99258 | 0.98037 | 0.99977 | 0.9855 | 0.99098 | 0.9976 | 0.99749 | 0.99041 | 0.99635 | 0.99258 | 0.9782 | 0.98037 | 1 | 0.8911
|  |  |  | 25 | 0.9895 | 0.99521 | 0.9992 | 0.99852 | 1 | 0.99977 | 0.99566 | 0.99566 | 0.99326 | 0.98733 | 0.98345 | 1 | 1 | 0.91792 | 0.9984 | 0.99589 | 0.9871 | 1 | 0.9895 | 0.99521 | 0.9992 | 0.99852 | 0.99566 | 0.9984 | 0.99589 | 0.98733 | 0.9871 | 1 | 0.91792
|  |  |  | 26 | 0.99372 | 0.99692 | 0.99966 | 0.99954 | 1 | 1 | 0.99817 | 0.9976 | 0.99532 | 0.99018 | 0.98756 | 1 | 1 | 0.92968 | 0.99909 | 0.99715 | 0.99075 | 1 | 0.99372 | 0.99692 | 0.99966 | 0.99954 | 0.99817 | 0.99909 | 0.99715 | 0.99018 | 0.99075 | 1 | 0.92968
|  |  |  | 27 | 0.99669 | 0.9984 | 1 | 1 | 1 | 1 | 0.9992 | 0.99932 | 0.99806 | 0.99543 | 0.99338 | 1 | 1 | 0.94897 | 0.99966 | 0.99886 | 0.99429 | 1 | 0.99669 | 0.9984 | 1 | 1 | 0.9992 | 0.99966 | 0.99886 | 0.99543 | 0.99429 | 1 | 0.94897
|  |  |  | 28 | 0.99874 | 0.9992 | 1 | 1 | 1 | 1 | 1 | 0.99989 | 0.99932 | 0.9976 | 0.99726 | 1 | 1 | 0.96461 | 1 | 0.99966 | 0.99658 | 1 | 0.99874 | 0.9992 | 1 | 1 | 1 | 1 | 0.99966 | 0.9976 | 0.99658 | 1 | 0.96461
|  |  |  | 29 | 0.99966 | 0.99977 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9992 | 0.99863 | 1 | 1 | 0.97671 | 1 | 1 | 0.99886 | 1 | 0.99966 | 0.99977 | 1 | 1 | 1 | 1 | 1 | 0.9992 | 0.99886 | 1 | 0.97671
|  |  |  | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99977 | 1 | 1 | 0.98527 | 1 | 1 | 0.99989 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99989 | 1 | 0.98527
|  |  |  | 31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98893 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98893
|  |  |  | 32 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99418 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99418
|  |  |  | 33 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99715 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99715
|  |  |  | 34 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99909 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99909
|  |  |  | 35 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943
|  |  |  | 36 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943
|  |  |  | 37 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | 38 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | 39 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | 40 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Säädata (hidden)
| Kielivalinta | Aloitus | Määrä
FALSE | Suomi | 0 | 4 |  | Suomi, TRY 2020 | [16 empty] | Valinta
TRUE | Muut | 4 | 13 |  | I (Vantaa) | II (Jokioinen) | III (Jyväskylä) | IV (Sodankylä) | SWE - Stockholm | SWE - Gothenburg | EST - Tallinn | LAT - Riga | LTU - Vilnius | POL - Warsaw | POL - Krakow | POL - Gdansk | ISL - Reykjavík | ROU - Bucharest | NOR - Oslo | DEN - Copenhagen | GER - Berlin | SWE - Stockholm | I (Vantaa) | II (Jokioinen) | III (Jyväskylä) | IV (Sodankylä) | EST - Tallinn | NOR - Oslo | DEN - Copenhagen | POL - Warsaw | GER - Berlin | ISL - Reykjavík | RO - Bucharest | LAT - Riga | LTU - Vilnius | POL - Gdansk | POL - Krakow | SWE - Stockholm | SWE - Gothenburg
| Valinta | 4 | 13 | -40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tallinna | Oslo | Köpis | Varsova | Berliini | Reyk | Buka | Riika | Vilna | Gdansk | Krakova | Stökis | Goteb
|  |  |  | -39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Otsikot |  |  |  | -38 | 0 | 0 | 0 | 0.00034247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I (Vantaa) |  | SWE - Stockholm |  | -37 | 0 | 0 | 0 | 0.00057078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00057078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
II (Jokioinen) |  | SWE - Gothenburg |  | -36 | 0 | 0 | 0 | 0.0011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0
III (Jyväskylä) |  | EST - Tallinn |  | -35 | 0 | 0 | 0 | 0.0018265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018265 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IV (Sodankylä) |  | LAT - Riga |  | -34 | 0 | 0 | 0 | 0.002968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002968 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWE - Stockholm |  | LTU - Vilnius |  | -33 | 0 | 0 | 0 | 0.0041096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041096 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWE - Gothenburg |  | POL - Warsaw |  | -32 | 0 | 0 | 0 | 0.0047945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047945 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EST - Tallinn |  | POL - Krakow |  | -31 | 0 | 0 | 0.00022831 | 0.0060502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00022831 | 0.0060502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAT - Riga |  | POL - Gdansk |  | -30 | 0 | 0 | 0.00034247 | 0.0079909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0.0079909 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LTU - Vilnius |  | ISL - Reykjavík |  | -29 | 0 | 0 | 0.00045662 | 0.011187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00045662 | 0.011187 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POL - Warsaw |  | ROU - Bucharest |  | -28 | 0 | 0 | 0.00091324 | 0.014726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00091324 | 0.014726 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POL - Krakow |  | NOR - Oslo |  | -27 | 0 | 0 | 0.0018265 | 0.019064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018265 | 0.019064 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POL - Gdansk |  | DEN - Copenhagen |  | -26 | 0 | 0.00034247 | 0.0026256 | 0.022489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0.0026256 | 0.022489 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ISL - Reykjavík |  | GER - Berlin |  | -25 | 0 | 0.00091324 | 0.0038813 | 0.027397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00091324 | 0.0038813 | 0.027397 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ROU - Bucharest |  |  |  | -24 | 0.00011416 | 0.0013699 | 0.0058219 | 0.030936 | 0 | 0 | 0 | 0 | 0.00011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00011416 | 0.0013699 | 0.0058219 | 0.030936 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOR - Oslo |  |  |  | -23 | 0.00034247 | 0.0023973 | 0.0073059 | 0.034018 | 0 | 0 | 0 | 0 | 0.0011416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034247 | 0.0023973 | 0.0073059 | 0.034018 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEN - Copenhagen |  |  |  | -22 | 0.00057078 | 0.002968 | 0.0083333 | 0.041096 | 0 | 0 | 0 | 0 | 0.0022831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00057078 | 0.002968 | 0.0083333 | 0.041096 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GER - Berlin |  |  |  | -21 | 0.0011416 | 0.0045662 | 0.010616 | 0.048059 | 0 | 0 | 0 | 0 | 0.0033105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011416 | 0.0045662 | 0.010616 | 0.048059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | -20 | 0.0028539 | 0.0058219 | 0.012671 | 0.055251 | 0 | 0 | 0 | 0 | 0.0055936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028539 | 0.0058219 | 0.012671 | 0.055251 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | -19 | 0.0053653 | 0.0077626 | 0.016553 | 0.062557 | 0 | 0 | 0 | 0.00034247 | 0.0063927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0053653 | 0.0077626 | 0.016553 | 0.062557 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | -18 | 0.0070776 | 0.010046 | 0.01895 | 0.068037 | 0 | 0 | 0 | 0.0025114 | 0.0070776 | 0.00034247 | 0 | 0 | 0 | 0 | 0.00045662 | 0 | 0 | 0 | 0.0070776 | 0.010046 | 0.01895 | 0.068037 | 0 | 0.00045662 | 0 | 0.00034247 | 0 | 0 | 0
1 | Valittu alue listasta |  |  | -17 | 0.0092466 | 0.013128 | 0.023288 | 0.074543 | 0 | 0 | 0.00022831 | 0.003653 | 0.0079909 | 0.0010274 | 0.00011416 | 0 | 0 | 0 | 0.0018265 | 0 | 0 | 0 | 0.0092466 | 0.013128 | 0.023288 | 0.074543 | 0.00022831 | 0.0018265 | 0 | 0.0010274 | 0 | 0 | 0
1 | Tarkastus, jos on suurempi ollut kuin suomen |  |  | -16 | 0.011872 | 0.018265 | 0.028539 | 0.081621 | 0 | 0.00022831 | 0.0012557 | 0.0098174 | 0.011301 | 0.0020548 | 0.0018265 | 0 | 0 | 0 | 0.0037671 | 0 | 0 | 0 | 0.011872 | 0.018265 | 0.028539 | 0.081621 | 0.0012557 | 0.0037671 | 0 | 0.0020548 | 0 | 0 | 0
|  |  |  | -15 | 0.016324 | 0.023288 | 0.035845 | 0.090982 | 0 | 0.0021689 | 0.0047945 | 0.012443 | 0.01347 | 0.0037671 | 0.0034247 | 0 | 0 | 0 | 0.0063927 | 0 | 0.00011416 | 0 | 0.016324 | 0.023288 | 0.035845 | 0.090982 | 0.0047945 | 0.0063927 | 0 | 0.0037671 | 0.00011416 | 0 | 0
5 | Siirtymä säädatalistassa |  |  | -14 | 0.021918 | 0.029795 | 0.043493 | 0.10422 | 0 | 0.0025114 | 0.0068493 | 0.013927 | 0.015639 | 0.0047945 | 0.0044521 | 0 | 0 | 0 | 0.0074201 | 0 | 0.00068493 | 0 | 0.021918 | 0.029795 | 0.043493 | 0.10422 | 0.0068493 | 0.0074201 | 0 | 0.0047945 | 0.00068493 | 0 | 0
SWE - Stockholm | Otsikko |  |  | -13 | 0.028653 | 0.03653 | 0.051598 | 0.11747 | 0 | 0.0035388 | 0.012557 | 0.01621 | 0.020205 | 0.0067352 | 0.0075342 | 0 | 0 | 0.00068493 | 0.011301 | 0 | 0.0015982 | 0 | 0.028653 | 0.03653 | 0.051598 | 0.11747 | 0.012557 | 0.011301 | 0 | 0.0067352 | 0.0015982 | 0 | 0.00068493
|  |  |  | -12 | 0.034589 | 0.041324 | 0.060959 | 0.13345 | 0.00034247 | 0.0073059 | 0.019749 | 0.019863 | 0.028995 | 0.0097032 | 0.01016 | 0.00034247 | 0 | 0.0050228 | 0.014041 | 0 | 0.0037671 | 0.00034247 | 0.034589 | 0.041324 | 0.060959 | 0.13345 | 0.019749 | 0.014041 | 0 | 0.0097032 | 0.0037671 | 0 | 0.0050228
|  |  |  | -11 | 0.040639 | 0.048402 | 0.071575 | 0.15137 | 0.0013699 | 0.012671 | 0.029224 | 0.02911 | 0.036073 | 0.013356 | 0.013813 | 0.0013699 | 0.0012557 | 0.010274 | 0.018721 | 0 | 0.0054795 | 0.0013699 | 0.040639 | 0.048402 | 0.071575 | 0.15137 | 0.029224 | 0.018721 | 0 | 0.013356 | 0.0054795 | 0.0012557 | 0.010274
|  |  |  | -10 | 0.046575 | 0.056963 | 0.083105 | 0.16861 | 0.0049087 | 0.015753 | 0.040297 | 0.036416 | 0.04589 | 0.018037 | 0.016553 | 0.0049087 | 0.003653 | 0.013584 | 0.021233 | 0.0025114 | 0.008105 | 0.0049087 | 0.046575 | 0.056963 | 0.083105 | 0.16861 | 0.040297 | 0.021233 | 0.0025114 | 0.018037 | 0.008105 | 0.003653 | 0.013584
|  |  |  | -9 | 0.05468 | 0.067352 | 0.097945 | 0.1863 | 0.0067352 | 0.01758 | 0.048744 | 0.039498 | 0.052055 | 0.020548 | 0.018721 | 0.0067352 | 0.0047945 | 0.015068 | 0.023174 | 0.0030822 | 0.0092466 | 0.0067352 | 0.05468 | 0.067352 | 0.097945 | 0.1863 | 0.048744 | 0.023174 | 0.0030822 | 0.020548 | 0.0092466 | 0.0047945 | 0.015068
|  |  |  | -8 | 0.063356 | 0.076256 | 0.11667 | 0.20091 | 0.0091324 | 0.02363 | 0.062557 | 0.048402 | 0.067009 | 0.025228 | 0.025685 | 0.0091324 | 0.0090183 | 0.02032 | 0.030365 | 0.0050228 | 0.012785 | 0.0091324 | 0.063356 | 0.076256 | 0.11667 | 0.20091 | 0.062557 | 0.030365 | 0.0050228 | 0.025228 | 0.012785 | 0.0090183 | 0.02032
|  |  |  | -7 | 0.075 | 0.087785 | 0.13699 | 0.22237 | 0.011301 | 0.031849 | 0.084475 | 0.068379 | 0.082763 | 0.034018 | 0.038699 | 0.011301 | 0.013356 | 0.028311 | 0.039041 | 0.0086758 | 0.016553 | 0.011301 | 0.075 | 0.087785 | 0.13699 | 0.22237 | 0.084475 | 0.039041 | 0.0086758 | 0.034018 | 0.016553 | 0.013356 | 0.028311
|  |  |  | -6 | 0.08847 | 0.10217 | 0.16096 | 0.24121 | 0.023858 | 0.042808 | 0.10616 | 0.0879 | 0.10582 | 0.049087 | 0.054338 | 0.023858 | 0.022717 | 0.039954 | 0.053539 | 0.014041 | 0.021804 | 0.023858 | 0.08847 | 0.10217 | 0.16096 | 0.24121 | 0.10616 | 0.053539 | 0.014041 | 0.049087 | 0.021804 | 0.022717 | 0.039954
|  |  |  | -5 | 0.10548 | 0.12317 | 0.18801 | 0.2718 | 0.042922 | 0.059018 | 0.13071 | 0.11347 | 0.13071 | 0.069977 | 0.070205 | 0.042922 | 0.041895 | 0.053995 | 0.074543 | 0.020662 | 0.028767 | 0.042922 | 0.10548 | 0.12317 | 0.18801 | 0.2718 | 0.13071 | 0.074543 | 0.020662 | 0.069977 | 0.028767 | 0.041895 | 0.053995
|  |  |  | -4 | 0.12888 | 0.14452 | 0.21393 | 0.30651 | 0.056849 | 0.07032 | 0.14772 | 0.12911 | 0.14874 | 0.083447 | 0.081735 | 0.056849 | 0.049429 | 0.063699 | 0.086872 | 0.028767 | 0.03516 | 0.056849 | 0.12888 | 0.14452 | 0.21393 | 0.30651 | 0.14772 | 0.086872 | 0.028767 | 0.083447 | 0.03516 | 0.049429 | 0.063699
|  |  |  | -3 | 0.15571 | 0.16849 | 0.24406 | 0.34178 | 0.080936 | 0.10148 | 0.1734 | 0.16598 | 0.19075 | 0.1153 | 0.10251 | 0.080936 | 0.078539 | 0.084932 | 0.11781 | 0.044292 | 0.048858 | 0.080936 | 0.15571 | 0.16849 | 0.24406 | 0.34178 | 0.1734 | 0.11781 | 0.044292 | 0.1153 | 0.048858 | 0.078539 | 0.084932
|  |  |  | -2 | 0.18425 | 0.19338 | 0.27728 | 0.37648 | 0.11107 | 0.13516 | 0.20468 | 0.20228 | 0.22911 | 0.15377 | 0.1339 | 0.11107 | 0.11724 | 0.11016 | 0.16244 | 0.071689 | 0.066324 | 0.11107 | 0.18425 | 0.19338 | 0.27728 | 0.37648 | 0.20468 | 0.16244 | 0.071689 | 0.15377 | 0.066324 | 0.11724 | 0.11016
|  |  |  | -1 | 0.20925 | 0.2234 | 0.3121 | 0.41678 | 0.15719 | 0.16667 | 0.23185 | 0.24463 | 0.271 | 0.19121 | 0.16929 | 0.15719 | 0.15571 | 0.1347 | 0.21119 | 0.10148 | 0.10091 | 0.15719 | 0.20925 | 0.2234 | 0.3121 | 0.41678 | 0.23185 | 0.21119 | 0.10148 | 0.19121 | 0.10091 | 0.15571 | 0.1347
|  |  |  | 0 | 0.2492 | 0.27089 | 0.36792 | 0.46027 | 0.21256 | 0.20468 | 0.27363 | 0.28938 | 0.30811 | 0.22979 | 0.20833 | 0.21256 | 0.20274 | 0.16381 | 0.25753 | 0.14212 | 0.13904 | 0.21256 | 0.2492 | 0.27089 | 0.36792 | 0.46027 | 0.27363 | 0.25753 | 0.14212 | 0.22979 | 0.13904 | 0.20274 | 0.16381
|  |  |  | 1 | 0.30993 | 0.34224 | 0.41005 | 0.51119 | 0.24155 | 0.225 | 0.30491 | 0.3105 | 0.32968 | 0.24521 | 0.22888 | 0.24155 | 0.23379 | 0.18014 | 0.28151 | 0.1637 | 0.16233 | 0.24155 | 0.30993 | 0.34224 | 0.41005 | 0.51119 | 0.30491 | 0.28151 | 0.1637 | 0.24521 | 0.16233 | 0.23379 | 0.18014
|  |  |  | 2 | 0.36918 | 0.40137 | 0.45171 | 0.54372 | 0.30034 | 0.27112 | 0.36507 | 0.3524 | 0.36724 | 0.27717 | 0.2653 | 0.30034 | 0.29498 | 0.21107 | 0.3355 | 0.20742 | 0.19806 | 0.30034 | 0.36918 | 0.40137 | 0.45171 | 0.54372 | 0.36507 | 0.3355 | 0.20742 | 0.27717 | 0.19806 | 0.29498 | 0.21107
|  |  |  | 3 | 0.41598 | 0.44018 | 0.48653 | 0.57363 | 0.34852 | 0.32523 | 0.40559 | 0.39064 | 0.40274 | 0.31324 | 0.30445 | 0.34852 | 0.35856 | 0.24612 | 0.38824 | 0.26221 | 0.24201 | 0.34852 | 0.41598 | 0.44018 | 0.48653 | 0.57363 | 0.40559 | 0.38824 | 0.26221 | 0.31324 | 0.24201 | 0.35856 | 0.24612
|  |  |  | 4 | 0.4508 | 0.47717 | 0.51838 | 0.61016 | 0.40251 | 0.36781 | 0.45342 | 0.4266 | 0.43436 | 0.3476 | 0.33938 | 0.40251 | 0.41587 | 0.28128 | 0.44189 | 0.31358 | 0.29486 | 0.40251 | 0.4508 | 0.47717 | 0.51838 | 0.61016 | 0.45342 | 0.44189 | 0.31358 | 0.3476 | 0.29486 | 0.41587 | 0.28128
|  |  |  | 5 | 0.48413 | 0.50776 | 0.54886 | 0.63642 | 0.44121 | 0.41747 | 0.49874 | 0.46575 | 0.46701 | 0.38368 | 0.37614 | 0.44121 | 0.48139 | 0.3226 | 0.48162 | 0.36598 | 0.34167 | 0.44121 | 0.48413 | 0.50776 | 0.54886 | 0.63642 | 0.49874 | 0.48162 | 0.36598 | 0.38368 | 0.34167 | 0.48139 | 0.3226
|  |  |  | 6 | 0.51587 | 0.54167 | 0.58139 | 0.66416 | 0.46187 | 0.43938 | 0.5161 | 0.47979 | 0.48881 | 0.40742 | 0.39475 | 0.46187 | 0.51941 | 0.34121 | 0.49772 | 0.39087 | 0.36553 | 0.46187 | 0.51587 | 0.54167 | 0.58139 | 0.66416 | 0.5161 | 0.49772 | 0.39087 | 0.40742 | 0.36553 | 0.51941 | 0.34121
|  |  |  | 7 | 0.55331 | 0.58744 | 0.60719 | 0.69053 | 0.50445 | 0.48276 | 0.55011 | 0.51598 | 0.52466 | 0.44806 | 0.43379 | 0.50445 | 0.59178 | 0.36861 | 0.53231 | 0.44315 | 0.41495 | 0.50445 | 0.55331 | 0.58744 | 0.60719 | 0.69053 | 0.55011 | 0.53231 | 0.44315 | 0.44806 | 0.41495 | 0.59178 | 0.36861
|  |  |  | 8 | 0.58984 | 0.62123 | 0.63162 | 0.71872 | 0.54589 | 0.53139 | 0.58858 | 0.54749 | 0.55925 | 0.48413 | 0.47066 | 0.54589 | 0.66039 | 0.3992 | 0.56667 | 0.49167 | 0.45879 | 0.54589 | 0.58984 | 0.62123 | 0.63162 | 0.71872 | 0.58858 | 0.56667 | 0.49167 | 0.48413 | 0.45879 | 0.66039 | 0.3992
|  |  |  | 9 | 0.61747 | 0.654 | 0.66233 | 0.74886 | 0.58037 | 0.58151 | 0.62055 | 0.58288 | 0.59509 | 0.52466 | 0.50925 | 0.58037 | 0.73002 | 0.43333 | 0.60137 | 0.54167 | 0.50377 | 0.58037 | 0.61747 | 0.654 | 0.66233 | 0.74886 | 0.62055 | 0.60137 | 0.54167 | 0.52466 | 0.50377 | 0.73002 | 0.43333
|  |  |  | 10 | 0.64395 | 0.68836 | 0.69623 | 0.78527 | 0.6218 | 0.62409 | 0.65936 | 0.6258 | 0.63402 | 0.56393 | 0.55251 | 0.6218 | 0.79886 | 0.46849 | 0.64578 | 0.59041 | 0.54909 | 0.6218 | 0.64395 | 0.68836 | 0.69623 | 0.78527 | 0.65936 | 0.64578 | 0.59041 | 0.56393 | 0.54909 | 0.79886 | 0.46849
|  |  |  | 11 | 0.67626 | 0.72169 | 0.73105 | 0.82283 | 0.64635 | 0.64566 | 0.68094 | 0.6484 | 0.65228 | 0.58425 | 0.57043 | 0.64635 | 0.83482 | 0.48664 | 0.67169 | 0.6129 | 0.57066 | 0.64635 | 0.67626 | 0.72169 | 0.73105 | 0.82283 | 0.68094 | 0.67169 | 0.6129 | 0.58425 | 0.57066 | 0.83482 | 0.48664
|  |  |  | 12 | 0.71416 | 0.75297 | 0.76781 | 0.85114 | 0.69669 | 0.69372 | 0.71861 | 0.69326 | 0.6895 | 0.62785 | 0.60696 | 0.69669 | 0.89909 | 0.51895 | 0.72568 | 0.6589 | 0.61963 | 0.69669 | 0.71416 | 0.75297 | 0.76781 | 0.85114 | 0.71861 | 0.72568 | 0.6589 | 0.62785 | 0.61963 | 0.89909 | 0.51895
|  |  |  | 13 | 0.75434 | 0.78493 | 0.80594 | 0.87603 | 0.74589 | 0.74258 | 0.76404 | 0.7339 | 0.72397 | 0.66998 | 0.65228 | 0.74589 | 0.94418 | 0.55468 | 0.7758 | 0.70742 | 0.67043 | 0.74589 | 0.75434 | 0.78493 | 0.80594 | 0.87603 | 0.76404 | 0.7758 | 0.70742 | 0.66998 | 0.67043 | 0.94418 | 0.55468
|  |  |  | 14 | 0.78733 | 0.81975 | 0.84509 | 0.89578 | 0.79064 | 0.79098 | 0.80936 | 0.77215 | 0.75822 | 0.71792 | 0.69087 | 0.79064 | 0.97648 | 0.59064 | 0.82249 | 0.75582 | 0.72329 | 0.79064 | 0.78733 | 0.81975 | 0.84509 | 0.89578 | 0.80936 | 0.82249 | 0.75582 | 0.71792 | 0.72329 | 0.97648 | 0.59064
|  |  |  | 15 | 0.82626 | 0.85468 | 0.87568 | 0.91804 | 0.83756 | 0.83927 | 0.84532 | 0.81084 | 0.79429 | 0.7621 | 0.72911 | 0.83756 | 0.99235 | 0.63037 | 0.8613 | 0.79966 | 0.77203 | 0.83756 | 0.82626 | 0.85468 | 0.87568 | 0.91804 | 0.84532 | 0.8613 | 0.79966 | 0.7621 | 0.77203 | 0.99235 | 0.63037
|  |  |  | 16 | 0.86187 | 0.88059 | 0.89909 | 0.9355 | 0.86473 | 0.86073 | 0.86313 | 0.83116 | 0.81199 | 0.78048 | 0.75103 | 0.86473 | 0.99509 | 0.64772 | 0.88299 | 0.82386 | 0.79349 | 0.86473 | 0.86187 | 0.88059 | 0.89909 | 0.9355 | 0.86313 | 0.88299 | 0.82386 | 0.78048 | 0.79349 | 0.99509 | 0.64772
|  |  |  | 17 | 0.88995 | 0.90388 | 0.921 | 0.95274 | 0.90559 | 0.89224 | 0.8895 | 0.86906 | 0.85046 | 0.82352 | 0.79018 | 0.90559 | 0.9984 | 0.68196 | 0.91781 | 0.86336 | 0.83253 | 0.90559 | 0.88995 | 0.90388 | 0.921 | 0.95274 | 0.8895 | 0.91781 | 0.86336 | 0.82352 | 0.83253 | 0.9984 | 0.68196
|  |  |  | 18 | 0.91358 | 0.9226 | 0.93893 | 0.96712 | 0.93619 | 0.92683 | 0.91461 | 0.90148 | 0.8879 | 0.86461 | 0.82774 | 0.93619 | 1 | 0.71826 | 0.94509 | 0.89874 | 0.86906 | 0.93619 | 0.91358 | 0.9226 | 0.93893 | 0.96712 | 0.91461 | 0.94509 | 0.89874 | 0.86461 | 0.86906 | 1 | 0.71826
|  |  |  | 19 | 0.93219 | 0.93836 | 0.95491 | 0.97603 | 0.96176 | 0.94886 | 0.93642 | 0.92626 | 0.91838 | 0.89452 | 0.86473 | 0.96176 | 1 | 0.75205 | 0.9637 | 0.92626 | 0.9032 | 0.96176 | 0.93219 | 0.93836 | 0.95491 | 0.97603 | 0.93642 | 0.9637 | 0.92626 | 0.89452 | 0.9032 | 1 | 0.75205
|  |  |  | 20 | 0.94783 | 0.95491 | 0.96701 | 0.98265 | 0.97637 | 0.96632 | 0.954 | 0.9508 | 0.94201 | 0.92123 | 0.89692 | 0.97637 | 1 | 0.78436 | 0.9766 | 0.94806 | 0.92842 | 0.97637 | 0.94783 | 0.95491 | 0.96701 | 0.98265 | 0.954 | 0.9766 | 0.94806 | 0.92123 | 0.92842 | 1 | 0.78436
|  |  |  | 21 | 0.96324 | 0.96758 | 0.97808 | 0.9879 | 0.98345 | 0.97329 | 0.96107 | 0.96199 | 0.95126 | 0.93288 | 0.91256 | 0.98345 | 1 | 0.80137 | 0.98174 | 0.95913 | 0.93973 | 0.98345 | 0.96324 | 0.96758 | 0.97808 | 0.9879 | 0.96107 | 0.98174 | 0.95913 | 0.93288 | 0.93973 | 1 | 0.80137
|  |  |  | 22 | 0.97283 | 0.97751 | 0.98653 | 0.99167 | 0.99155 | 0.98436 | 0.97306 | 0.97409 | 0.96644 | 0.95091 | 0.93516 | 0.99155 | 1 | 0.83105 | 0.98847 | 0.97454 | 0.95685 | 0.99155 | 0.97283 | 0.97751 | 0.98653 | 0.99167 | 0.97306 | 0.98847 | 0.97454 | 0.95091 | 0.95685 | 1 | 0.83105
|  |  |  | 23 | 0.98082 | 0.98539 | 0.99304 | 0.99498 | 0.99692 | 0.99269 | 0.98265 | 0.98413 | 0.97785 | 0.96712 | 0.95525 | 0.99692 | 1 | 0.86107 | 0.99372 | 0.98562 | 0.96986 | 0.99692 | 0.98082 | 0.98539 | 0.99304 | 0.99498 | 0.98265 | 0.99372 | 0.98562 | 0.96712 | 0.96986 | 1 | 0.86107
|  |  |  | 24 | 0.9855 | 0.99098 | 0.9976 | 0.99749 | 0.99977 | 0.9976 | 0.99041 | 0.99132 | 0.98733 | 0.9782 | 0.97112 | 0.99977 | 1 | 0.8911 | 0.99635 | 0.99258 | 0.98037 | 0.99977 | 0.9855 | 0.99098 | 0.9976 | 0.99749 | 0.99041 | 0.99635 | 0.99258 | 0.9782 | 0.98037 | 1 | 0.8911
|  |  |  | 25 | 0.9895 | 0.99521 | 0.9992 | 0.99852 | 1 | 0.99977 | 0.99566 | 0.99566 | 0.99326 | 0.98733 | 0.98345 | 1 | 1 | 0.91792 | 0.9984 | 0.99589 | 0.9871 | 1 | 0.9895 | 0.99521 | 0.9992 | 0.99852 | 0.99566 | 0.9984 | 0.99589 | 0.98733 | 0.9871 | 1 | 0.91792
|  |  |  | 26 | 0.99372 | 0.99692 | 0.99966 | 0.99954 | 1 | 1 | 0.99817 | 0.9976 | 0.99532 | 0.99018 | 0.98756 | 1 | 1 | 0.92968 | 0.99909 | 0.99715 | 0.99075 | 1 | 0.99372 | 0.99692 | 0.99966 | 0.99954 | 0.99817 | 0.99909 | 0.99715 | 0.99018 | 0.99075 | 1 | 0.92968
|  |  |  | 27 | 0.99669 | 0.9984 | 1 | 1 | 1 | 1 | 0.9992 | 0.99932 | 0.99806 | 0.99543 | 0.99338 | 1 | 1 | 0.94897 | 0.99966 | 0.99886 | 0.99429 | 1 | 0.99669 | 0.9984 | 1 | 1 | 0.9992 | 0.99966 | 0.99886 | 0.99543 | 0.99429 | 1 | 0.94897
|  |  |  | 28 | 0.99874 | 0.9992 | 1 | 1 | 1 | 1 | 1 | 0.99989 | 0.99932 | 0.9976 | 0.99726 | 1 | 1 | 0.96461 | 1 | 0.99966 | 0.99658 | 1 | 0.99874 | 0.9992 | 1 | 1 | 1 | 1 | 0.99966 | 0.9976 | 0.99658 | 1 | 0.96461
|  |  |  | 29 | 0.99966 | 0.99977 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9992 | 0.99863 | 1 | 1 | 0.97671 | 1 | 1 | 0.99886 | 1 | 0.99966 | 0.99977 | 1 | 1 | 1 | 1 | 1 | 0.9992 | 0.99886 | 1 | 0.97671
|  |  |  | 30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99977 | 1 | 1 | 0.98527 | 1 | 1 | 0.99989 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99989 | 1 | 0.98527
|  |  |  | 31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98893 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98893
|  |  |  | 32 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99418 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99418
|  |  |  | 33 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99715 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99715
|  |  |  | 34 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99909 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99909
|  |  |  | 35 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943
|  |  |  | 36 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99943
|  |  |  | 37 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | 38 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | 39 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | 40 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Kojeet ja kennon hyötysuhde (hidden)
[8 empty] | Vanha |  |  | LTO-arvot A. Pulkkasen sähköpostilla antaman ehdotuksen mukaisesti (8.2.2024)
Kojevalinta | 7 |  | Tunnus | Malli | Min. qV | Maks. qV | Jäteilman raj. | n, tulo | EN 13141-7 | EN 308 | Laskentaohjelmassa V. 5,8 | [7 empty] | AIEMMAT ARVOT |  |  |  | Ehdotus
Jäteilma | -6.5 |  | 1 | Airfi model 60 | 18 | 100 | -6.5 | 79.5% | - | - | [12 empty] | versio 5.9 ja seuraavat
Min. qV | 10 |  | 2 | Airfi model 100 | 18 | 100 | -6.5 | 82.5% | - | -
Maks. qV | 130 |  | 3 | Airfi model 150 | 30 | 170 | -6.5 | 79.5% | - | - |  | Ohjelmassa NRLTO=1, nyt
n, tulostus | 0% |  | 4 | Airfi model 250 | 30 | 260 | -6.5 | 79.5% | - | -
|  |  | 5 | Airfi Model 350 | 30 | 360 | -6.5 | 79.5% | - | -
|  |  | 6 | Airfi Model 130 | 20 | 130 | -6.5 | 77.5% | - | - |  | Model 60, 79,5 % | [5 empty] | Model 60
|  |  | 7 | Airfi Model 53mini | 10 | 130 | -6.5 |  | 80.35% | 81.65% |  | Model 100, 82,5 % | [5 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 60-kone, mitattu Zenner |  |  | dm³/s | Model 60nykyinen NRLTO=1 | EHDOTUS, model 60, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 60
[12 empty] | Model 130, 77,5 % | [6 empty] | 25 |  |  |  | 18 | 79.5 | 79.8 | 81.75
Muutokset versioon 6.0 | [11 empty] | Model 150, 79,5 % | [5 empty] | 3.4 | 34 | 80.1 |  |  | 28 | 79.5 | 79.7 | 81.5
Aiemmissa versioissa ollut fiksattu arvo 79,5 % Model 60,100, 130 ja 150 | [17 empty] | 3.8 | 43 | 80.7 |  |  | 36 | 79.5 | 79.6 | 81
Aiemmissa versioissa ollut tilavuusvirrasta riippuva laskenta Model 250/350 (79.5 % - 77.3 %) | [11 empty] | Model 250 ja Model 350 muuttuva | [5 empty] | 5.9 | 74 | 81.5 |  |  | 61.5 | 79.5 | 79.5 | 80.3
Versioon 6.0 iso muutos, ja käytetään A. Pulkkasen ohjeen mukaan tilavuusvirtariippuvaista laskentaa jokaisella mallilla | [12 empty] | ilmavirta | arvo |  |  |  | 9.2 | 108 | 83.1 |  |  | 90 | 79.5 | 78.5 | 79.5
Versiossa 7.2 otettu mukaan Model 53mini, samalla laskentaperiatteella kuin muutkin koneet, eli tilavuusvirtaperusteinen arvo. | [12 empty] | 50 | 79.5 |  |  |  |  | 130 |  |  |  | 130 | 79.5 | 78 | 78.2
[13 empty] | 100 | 79.5 | [8 empty] | 130 | 79.5 | 78 | 78.2
[13 empty] | 150 | 79.5
[13 empty] | 200 | 79.3
Laitevalinta | 7 | Airfi Model 53mini | [10 empty] | 250 | 78.2
[13 empty] | 300 | 77.5
[13 empty] | 350 | 77.3 |  |  |  | Model 100
Tilavuusvirta [dm³/s] | Arvo versioon v5.9 saakka | EN 13141-7 Nt(RLTO=1) | EN 308 | [14 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 100-kone, mitattu Zenner |  |  | dm³/s | Model 100nykyinen NRLTO=1 | EHDOTUS, model 100, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 100
15 | 0 | 80.5 | 81.8 | [15 empty] | 25 |  |  |  | 18 | 82.5 | 82.5 | 84
28 | 0 | 80.3 | 81.6 | [14 empty] | 3.6 | 34 | 82.7 |  |  | 29 | 82.5 | 82.5 | 83.7
36 | 0 | 80 | 81.2 | [14 empty] | 4.2 | 43 | 82.3 |  |  | 36 | 82.5 | 82.5 | 83.5
61.5 | 0 | 79.7 | 80.25 | [14 empty] | 6.1 | 71 | 83.2 |  |  | 60 | 82.5 | 82.4 | 83.2
90 | 0 | 79 | 79.3 | [14 empty] | 9.7 | 107 | 84.8 |  |  | 90 | 82.5 | 81.5 | 82
130 | 0 | 78 | 78 | [15 empty] | 130 |  |  |  | 130 | 82.5 | 80 | 80.2
130 | 0 | 78 | 78 | [19 empty] | 130 | 82.5 | 80 | 80.2
| qV | EN 13141-7 | EN 308
Min | 15 | 80.5 | 81.8
Max | 130 | 78 | 78 | [14 empty] | Model 130
[18 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 130-kone, simuloitu |  |  | dm³/s | Model 130nykyinen NRLTO=1 | EHDOTUS, model 130, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 130
Mitoitus qV | 25 | [17 empty] | 25 |  |  |  | 18 | 77.5 | 77.5 | 79.5
Tarkistus min/max | 25 | [17 empty] | 34 | 77.5 |  |  | 29 | 77.5 | 77.5 | 79
EN 13141-7 | 80.3462 | 80.35% | [16 empty] | 43 | 77.5 |  |  | 36 | 77.5 | 77.5 | 78.5
EN 308 | 81.6462 | 81.65% | [16 empty] | 71 | 77.5 |  |  | 60 | 77.5 | 77 | 77.5
[19 empty] | 107 | 77.5 |  |  | 90 | 77.5 | 75.5 | 76
[19 empty] | 140 |  |  |  | 140 | 77.5 | 73.5 | 74
Aputaulukko | EN 13141-7 | EN 308 | [20 empty] | 140 | 77.5 | 73.5 | 74
15 | 80.5 | 81.8
28 | 80.3 | 81.6
Model 150
[18 empty] | ohjaus V | g/s | tuloilman lämpötilahyötysuhde 150-kone, mitattu Zenner |  |  | dm³/s | Model 150nykyinen NRLTO=1 | EHDOTUS, model 150, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 150
Kielivalinta | [18 empty] | 25 |  |  |  | 18 | 79.5 | 79.5 | 82
Suomi | FALSE | [16 empty] | 3,8/3,8 | 68 | 79.3 |  |  | 29 | 79.5 | 79.5 | 81.75
Muut | TRUE | [16 empty] | 4,6/4,2 | 91 | 79.5 |  |  | 36 | 79.5 | 79.5 | 81.5
[18 empty] | 7,4/6,1 | 127 | 76.6 |  |  | 80 | 79.5 | 79.5 | 80.5
Syöttö | 90 | m³/h | [15 empty] | 10/8 | 167 | 79.9 |  |  | 120 | 79.5 | 79.5 | 80
Laskentaan | 25 | l/s | [16 empty] | 200 |  |  |  | 180 | 79.5 | 79 | 79.5
[20 empty] | ilmeisesti poikkeama kohdassa 76,6 |  |  | 180 | 79.5 | 79 | 79.5
Model 250 / 350
[19 empty] | dm³/s |  |  |  | dm³/s | Model 250-350 nykyinen NRLTO=1 | EHDOTUS, model 250-350, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 250-350
[19 empty] | 50 | 79.5 |  |  | 50 | 79.5 | 79.5 | 81
[19 empty] | 100 | 79.5 |  |  | 100 | 79.5 | 79.5 | 80.5
[19 empty] | 150 | 79.5 |  |  | 150 | 79.5 | 79.5 | 80
[19 empty] | 200 | 79.3 |  |  | 200 | 79.3 | 79 | 79.5
[19 empty] | 250 | 78.2 |  |  | 250 | 78.2 | 78.2 | 78.7
[19 empty] | 300 | 77.5 |  |  | 300 | 77.5 | 77.5 | 78
[19 empty] | 350 | 77.3 |  |  | 350 | 77.3 | 76.8 | 77
[18 empty] | Model 53mini, arvot saatu Pulkkasen mailista 16.4.2025 | [9 empty] | Pulkkasen mailista 16.4.2025
Model 53mini
[19 empty] | dm³/s |  |  |  | dm³/s | Model 250-350 nykyinen NRLTO=1 | EHDOTUS, model 250-350, EN 13141-7 1:1 Nt(RLTO=1) | Ehdotus EN308 model 250-350
[23 empty] | 15 |  | 80.5 | 81.8
[23 empty] | 28 |  | 80.3 | 81.6
[23 empty] | 36 |  | 80 | 81.2
[23 empty] | 61.5 |  | 79.7 | 80.25
[23 empty] | 90 |  | 79 | 79.3
[23 empty] | 130 |  | 78 | 78
[23 empty] | 130 |  | 78 | 78
Vanhaa laskentaa --> EI KÄYTÖSSÄ | [15 empty] | Airfi Model 300
Airfi model 60 | [15 empty] | Nykyinen MODEL 150 kenno
LEV-455-230, pituus 350 mm, s=2.3 mm | [15 empty] | ARVOT EKOCOIL OPTIMIZER, LEV-620-394-500-(lamelli 2,2) |  |  |  | MODEL 150 |  | MODEL 300 (nyk kenno)
[17 empty] | LAMELLIVÄLI 2,2 mm |  |  | lamelliväli 2,2 |  | lamelliväli 2,2
[16 empty] | Ilmavirta , m³/s | Hyötysuhde (tulo 2,2), model 150 | Hyötysuhde (poisto) | Painehäviö 2,2 | nykyinen arvo- koneen hyötysuhde MODEL 150 | laskettu- koneen vuosi hyötysuhde MODEL 150 | ajatus koneen lämpötilahyöstysuhde (model 300) | mistä laskettu model 300 vuosihyötysuhde
Tulko | 7 | 50%RH | [12 empty] | dm3/s | 0.05 | 83.5 | 84 | 19 | 79.5 | 76.1 | 79.5 | 76.1
Tpoisto | 20 | 50%RH | [12 empty] | 50 | 0.075 | 81.5 | 82 | 33 | 79.5 | 76.1 | 79.5 | 76.1
[15 empty] | 75 | 0.1 | 80.2 | 80.7 | 48 | 79.5 | 76.1 | 79.5 | 76.1
qV | n, tulo | [13 empty] | 100 | 0.15 | 78.5 | 78.9 | 85 | 79.5 | 76.1 | 79.5 | 76.1
100 | 78.1% | [13 empty] | 150 | 0.2 | 77.2 | 77.6 | 126 | ei alueella | ei alueella | 77.2 | 74.5
90 | 78.4% | [13 empty] | 200 | 0.25 | 76.2 | 76.7 | 168 | ei alueella | ei alueella | 76.2 | 74.1
80 | 78.7% | [13 empty] | 250 | 0.3 | 75.6 | 76.1 | 231 | ei alueella | ei alueella | 75.6 | 73.6
70 | 79.1% | [13 empty] | 300 | 0.35 | 75.3 | 75.8 | 306 | ei alueella | ei alueella | 75.3 | 73.6
60 | 79.5% | [13 empty] | 350
50 | 80.2% | [25 empty] | Käytetään tätä (huom. Versioon 5.9 saakka, tämän jälkeen tuli muutos)
40 | 81.3%
30 | 83.4%
22 | 86.4% | [21 empty] | Max | 83.5 |  |  |  | Max | 79.5
6.6314e-09 | -2.017e-06 | 0.00022914 | -0.011912 | 1.0348 | [18 empty] | Min | 75.3 |  |  |  | Min | 77.26%
qV, tulo | [22 empty] | -0.054191 | 4.635 | 103.024 |  |  | 7.681e-05 | -0.055722 | 87.3508
qV, poisto
qV, mitoitus | [22 empty] | Mitoituspiste, tuloilma |  |  |  |  | Mitoituspiste, tuloilma
n, tulo, mitoitus | [22 empty] | 25 | dm3/s |  |  |  | 25 | dm3/s
[23 empty] | 86.5332 | % |  |  |  | 86.0057 | %
Airfi model 100 | [22 empty] | 83.5% |  |  |  |  | 79.5%
LEV-500-270, pituus 350 mm, s=2 mm
Tulko | 7 | 50%RH | [13 empty] | USANON LASKENTA
Tpoisto | 20 | 50%RH | [13 empty] | Tuloilmapuhallin |  |  | Lämpötilat |  |  |  |  | Lämpötilahyötysuhteet
[16 empty] | Tilavuusvirta | Paine-ero | Hyötysuhde | Ulkoilma | Tuloilma | Poistoilma | Jäteilma | Lämpötilan nousu puhaltimessa | LTO-kennon tuloilman lämpötila-hyötysuhde | Koneen tuloilman lämpötila-hyötysuhde | Koneen tuloilman lämpötilahyötysuhde puhaltimen sähkötehosta puolet huomioiden
qV | n, tulo | [14 empty] | 50 | 89.8756 | 30% | -26 | 11.365 | 21 | -16.365 | 0.24965 | 83.5% | 79.5% | 79.5% | 79.5
120 | 79.1% | [14 empty] | 100 | 159.5023 | 35% | -26 | 11.365 | 21 | -16.365 | 0.37977 | 81.5% | 79.5% | 79.5% | 79.5
100 | 79.7% | [14 empty] | 150 | 246.3801 | 40% | -26 | 11.365 | 21 | -16.365 | 0.51329 | 80.2% | 79.5% | 79.5% | 79.5
90 | 80.1% | [14 empty] | 200 | 349.1202 | 40% | -26 | 10.895 | 21 | -16.365 | 0.72733 | 78.5% | 78.5% | 79.27% | 79.2738
70 | 81.3% | [14 empty] | 250 | 467.3753 | 40% | -26 | 10.284 | 21 | -16.365 | 0.9737 | 77.2% | 77.2% | 78.24% | 78.2358
60 | 82.1% | [14 empty] | 300 | 601.0204 | 40% | -26 | 9.814 | 21 | -16.365 | 1.2521 | 76.2% | 76.2% | 77.53% | 77.532
50 | 83.1% | [14 empty] | 350 | 750 | 40% | -26 | 9.532 | 21 | -16.365 | 1.5625 | 75.6% | 75.6% | 77.26% | 77.2622
40 | 84.3%
30 | 85.9%
25 | 87%
1.0827e-09 | -3.8382e-07 | 5.5261e-05 | -0.0042806 | 0.94769
qV, tulo | 0
qV, poisto | 0
qV, mitoitus | 0
n, tulo, mitoitus | 85%
Airfi model 150
LEV-455-230, pituus 350 mm, s=2.3 mm
Tulko | 7 | 50%RH
Tpoisto | 20 | 50%RH
qV | n, tulo
100
90
80
70
60
50
40
30
22
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
qV, tulo | 0
qV, poisto | 0
qV, mitoitus | 0
n, tulo, mitoitus | #VALUE!

## Laskenta keittiöohitus 53mini (hidden)
Poistopuolen mitoituspiste
qV | 26.9444 | dm3/s
Pd | 100 | Pa
Vohj | 4.3915 | V
Äänitehotasot kanavaan | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | Lw | LwA
Poisto | 62.4915 | 59.4915 | 50.4915 | 38.4915 | 34.4915 | 20.4915 | 14.4915 | 20.4915 | 64.4505 | 46.8138
Jäte | 72.7853 | 67.7853 | 62.7853 | 57.7853 | 55.7853 | 48.7853 | 39.7853 | 28.7853 |  | 60.912
| 55% | 60% | 70% | 70% | 70% | 65% | 60% | 55% | Lw | LwA
Painotettu keskiarvo | 68.1531 | 64.4678 | 59.0972 | 51.9972 | 49.3972 | 38.8825 | 29.6678 | 25.0531 | 70.1704 | 55.693
a-painotus | -26.2 | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1

## Laskenta_vuosihyötysuhde (hidden)
| Hakee arvot tulostus-välilehdeltä. |  |  |  | -26 |  | 21 | -6.5 | -6.5 | -6.5 | 21 | 21 | 3.6389 |  | 0.92784 | 63.06% | 58.51%
| Älä muuta tästä! | [17 empty] | Total | 4410.75 | 3676.5261 | 3411.2098
| Sisälämpötila | 21 | °C |  | tu | Aika vuodessa | tLTO,maks | tj | tj,min | tj,maks | tj, korjaamaton | tsisä | tLTO | tLTO, korjaamaton | RLTO | ηt | ηp | ηt, korjaamaton | ηp,korjaamaton | SS,Kd | ST,Kd | SJ,Kd
| Tuloilmamäärä | 25 | l/s |  | -32 | 0 | 21 | -6.5 | -6.5 | -6.5 | -19.9894 | 21 | -2.3611 | 15.6135 | 0.92784 | 55.92% | 51.89% | 83.35% | 77.34% | 0 | 0 | 0 | #VALUE! | #VALUE! | Ilmanvaihdon kokonaisenergiantarve |  | 3443.2785 | kWh
| Poistoilmamäärä | 26.9444 | l/s |  | -31 | 0 | 21 | -6.5 | -6.5 | -6.5 | -19.216 | 21 | -1.3611 | 15.7152 | 0.92784 | 57% | 52.88% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0 | Talteenotettu lämmitysenergia |  | 2662.9814 | kWh | Teho (puhaltimet + elektroniikka)
| RLTO | 0.92784 |  |  | -30 | 0 | 21 | -6.5 | -6.5 | -6.5 | -18.4427 | 21 | -0.36111 | 15.8168 | 0.92784 | 58.12% | 53.92% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0 | Ilmanvaihtokoneen energiankulutus |  | 330.6971 | kWh | 37.7508 | W
| nLTO 1 | 80.35% |  |  | -29 | 0 | 21 | -6.5 | -6.5 | -6.5 | -17.6693 | 21 | 0.63889 | 15.9184 | 0.92784 | 59.28% | 55% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
| nLTO, RT | 83.35% |  |  | -28 | 0 | 21 | -6.5 | -6.5 | -6.5 | -16.8959 | 21 | 1.6389 | 16.02 | 0.92784 | 60.49% | 56.12% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
| Minimi jäteilma | -6.5 | °C |  | -27 | 0 | 21 | -6.5 | -6.5 | -6.5 | -16.1225 | 21 | 2.6389 | 16.1217 | 0.92784 | 61.75% | 57.29% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0 | Tavoitelämpötila |  | 0
| Maksimi tLTO | 21 | °C |  | -26 | 0 | 21 | -6.5 | -6.5 | -6.5 | -15.3491 | 21 | 3.6389 | 16.2233 | 0.92784 | 63.06% | 58.51% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0 | tLTO (LTO jälkeinen lämpötila mitoitusolosuhteessa) |  | 17.5043
KS. säädata | Maa | 1 |  | 1 | -25 | 0 | 21 | -6.5 | -6.5 | -6.5 | -14.5757 | 21 | 4.6389 | 16.3249 | 0.92784 | 64.43% | 59.78% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
välilehti | Vyöhyke | 1 |  | 1 | -24 | 0 | 21 | -6.5 | -6.5 | -6.5 | -13.8023 | 21 | 5.6389 | 16.4266 | 0.92784 | 65.86% | 61.11% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0 | Jälkilämmityspatterin ottoteho |  | -525.1287 | W
| Muut poistoilmavirrat ei LTO:n kautta | 0 | l/s |  | -23 | 0 | 21 | -6.5 | -6.5 | -6.5 | -13.029 | 21 | 6.6389 | 16.5282 | 0.92784 | 67.36% | 62.5% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0 |  | Tulostus | - | W
| Käyttöaika / vrk | 0 | h |  | -22 | 0 | 21 | -6.5 | -6.5 | -6.5 | -12.2556 | 21 | 7.6389 | 16.6298 | 0.92784 | 68.93% | 63.95% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
| Poistoilma, kaikki | 26.9444 | l/s |  | -21 | 0 | 21 | -6.5 | -6.5 | -6.5 | -11.4822 | 21 | 8.6389 | 16.7315 | 0.92784 | 70.57% | 65.48% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
| Koko IV:n RT | 0.92784 |  |  | -20 | 0 | 21 | -6.5 | -6.5 | -6.5 | -10.7088 | 21 | 9.6389 | 16.8331 | 0.92784 | 72.29% | 67.07% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
HUOM! | Mitoittava ulkoLT | -26 | °C |  | -19 | 0 | 21 | -6.5 | -6.5 | -6.5 | -9.9354 | 21 | 10.6389 | 16.9347 | 0.92784 | 74.1% | 68.75% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
| Tuloilman LT, mit. | 3.6389 | °C |  | -18 | 0 | 21 | -6.5 | -6.5 | -6.5 | -9.162 | 21 | 11.6389 | 17.0364 | 0.92784 | 76% | 70.51% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
[5 empty] | -17 | 0 | 21 | -6.5 | -6.5 | -6.5 | -8.3886 | 21 | 12.6389 | 17.138 | 0.92784 | 78% | 72.37% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
[5 empty] | -16 | 0 | 21 | -6.5 | -6.5 | -6.5 | -7.6153 | 21 | 13.6389 | 17.2396 | 0.92784 | 80.11% | 74.32% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
[5 empty] | -15 | 0 | 21 | -6.5 | -6.5 | -6.5 | -6.8419 | 21 | 14.6389 | 17.3413 | 0.92784 | 82.33% | 76.39% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
| VUOSIHYÖTYSUHDE |  | 77.34% |  | -14 | 0 | 21 | -6.0685 | -6.0685 | -6.0685 | -6.0685 | 21 | 15.1738 | 17.4429 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
[5 empty] | -13 | 0 | 21 | -5.2951 | -5.2951 | -5.2951 | -5.2951 | 21 | 15.3403 | 17.5445 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 0 | 0 | 0 | 0 | 0
[5 empty] | -12 | 0.00034247 | 21 | -4.5217 | -4.5217 | -4.5217 | -4.5217 | 21 | 15.5067 | 17.6462 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 4.125 | 3.4383 | 3.1902 | 3.2202 | 2.4905
[5 empty] | -11 | 0.0013699 | 21 | -3.7483 | -3.7483 | -3.7483 | -3.7483 | 21 | 15.6732 | 17.7478 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 12 | 10.0025 | 9.2806 | 9.3679 | 7.245
[5 empty] | -10 | 0.0049087 | 21 | -2.9749 | -2.9749 | -2.9749 | -2.9749 | 21 | 15.8397 | 17.8494 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 40.0417 | 33.3762 | 30.9676 | 31.2588 | 24.1751
[5 empty] | -9 | 0.0067352 | 21 | -2.2016 | -2.2016 | -2.2016 | -2.2016 | 21 | 16.0061 | 17.9511 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 20 | 16.6708 | 15.4677 | 15.6131 | 12.075
[5 empty] | -8 | 0.0091324 | 21 | -1.4282 | -1.4282 | -1.4282 | -1.4282 | 21 | 16.1726 | 18.0527 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 25.375 | 21.151 | 19.6247 | 19.8091 | 15.3201
| Tuloilman rajoitus (muutos v.6.0) |  |  |  | -7 | 0.011301 | 21 | -0.65479 | -0.65479 | -0.65479 | -0.65479 | 21 | 16.3391 | 18.1543 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 22.1667 | 18.4768 | 17.1434 | 17.3045 | 13.3831
| No limitation |  |  |  | -6 | 0.023858 | 21 | 0.11859 | 0.11859 | 0.11859 | 0.11859 | 21 | 16.5055 | 18.2559 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 123.75 | 103.1503 | 95.7064 | 96.6062 | 74.7138
| Limited |  |  |  | -5 | 0.042922 | 21 | 0.89198 | 0.89198 | 0.89198 | 0.89198 | 21 | 16.672 | 18.3576 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 180.9167 | 150.8009 | 139.9183 | 141.2337 | 109.2281
| Valinta | 1 |  |  | -4 | 0.056849 | 21 | 1.6654 | 1.6654 | 1.6654 | 1.6654 | 21 | 16.8384 | 18.4592 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 127.0833 | 105.9287 | 98.2844 | 99.2084 | 76.7263
|  | No limitation |  |  | -3 | 0.080936 | 21 | 2.4387 | 2.4387 | 2.4387 | 2.4387 | 21 | 17.0049 | 18.5608 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 211 | 175.8764 | 163.1843 | 164.7184 | 127.3908
[5 empty] | -2 | 0.11107 | 21 | 3.2121 | 3.2121 | 3.2121 | 3.2121 | 21 | 17.1714 | 18.6625 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 253 | 210.885 | 195.6665 | 197.506 | 152.7482
| Tuloilma rajoitus | FALSE |  |  | -1 | 0.15719 | 21 | 3.9855 | 3.9855 | 3.9855 | 3.9855 | 21 | 17.3378 | 18.7641 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 370.3333 | 308.6868 | 286.4104 | 289.1029 | 223.588
| Syöttöarvon muotoilu | TRUE |  |  | 0 | 0.21256 | 21 | 4.7589 | 4.7589 | 4.7589 | 4.7589 | 21 | 17.5043 | 18.8657 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 424.375 | 353.7325 | 328.2054 | 331.2909 | 256.2156
[5 empty] | 1 | 0.24155 | 21 | 5.5323 | 5.5323 | 5.5323 | 5.5323 | 21 | 17.6708 | 18.9674 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 211.6667 | 176.4321 | 163.6999 | 165.2389 | 127.7933
| Sisälämpötila | 21 |  |  | 2 | 0.30034 | 21 | 6.3057 | 6.3057 | 6.3057 | 6.3057 | 21 | 17.8372 | 19.069 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 407.7083 | 339.8402 | 315.3157 | 318.28 | 246.1531
| Maksimi asetus | 20 |  |  | 3 | 0.34852 | 21 | 7.0791 | 7.0791 | 7.0791 | 7.0791 | 21 | 18.0037 | 19.1706 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 316.5 | 263.8147 | 244.7765 | 247.0776 | 191.0862
| Max tLTO valinta | 21 |  |  | 4 | 0.40251 | 21 | 7.8524 | 7.8524 | 7.8524 | 7.8524 | 21 | 18.1701 | 19.2723 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 335.0417 | 279.2698 | 259.1163 | 261.5523 | 202.2807
[5 empty] | 5 | 0.44121 | 21 | 8.6258 | 8.6258 | 8.6258 | 8.6258 | 21 | 18.3366 | 19.3739 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 226 | 188.3795 | 174.7851 | 176.4283 | 136.447
| Huomioteksti |  |  |  | 6 | 0.46187 | 21 | 9.3992 | 9.3992 | 9.3992 | 9.3992 | 21 | 18.5031 | 19.4755 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 113.125 | 94.2939 | 87.4892 | 88.3117 | 68.299
| FALSE |  |  |  | 7 | 0.50445 | 21 | 10.1726 | 10.1726 | 10.1726 | 10.1726 | 21 | 18.6695 | 19.5772 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 217.5833 | 181.3639 | 168.2758 | 169.8577 | 131.3655
| Huom. YM monisteen 122 mukaisesti laskettuna tuloilman maksimilämpötilan rajoitus voi olla käytössä tai sitä ei tarvitse huomioida. Todellisuudessa rakennuksen energiankulutusta arvioitaessa tulee huomioida, että kaikkea kennon talteenottamaa lämpöenergiaa ei voida hyödyntää. |  |  |  | 8 | 0.54589 | 21 | 10.946 | 10.946 | 10.946 | 10.946 | 21 | 18.836 | 19.6788 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 196.625 | 163.8943 | 152.0669 | 153.4965 | 118.7119
[5 empty] | 9 | 0.58037 | 21 | 11.7194 | 11.7194 | 11.7194 | 11.7194 | 21 | 19.0025 | 19.7804 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 151 | 125.8642 | 116.7812 | 117.8791 | 91.1659
[5 empty] | 10 | 0.6218 | 21 | 12.4928 | 12.4928 | 12.4928 | 12.4928 | 21 | 19.1689 | 19.8821 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 166.375 | 138.6798 | 128.672 | 129.8816 | 100.4486
[5 empty] | 11 | 0.64635 | 21 | 13.2661 | 13.2661 | 13.2661 | 13.2661 | 21 | 19.3354 | 19.9837 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 89.5833 | 74.6711 | 69.2824 | 69.9338 | 54.0858
[5 empty] | 12 | 0.69669 | 21 | 14.0395 | 14.0395 | 14.0395 | 14.0395 | 21 | 19.5018 | 20.0853 | 0.92784 | 83.35% | 77.34% | 83.35% | 77.34% | 165.375 | 137.8463 | 127.8986 | 129.101 | 99.8448
[23 empty] | 3443.2785 | 2662.9814
[5 empty] | Jälkilämmityspatterin ottotehon mitoitukseen | [17 empty] | kWh | kWh
[5 empty] | 0 | [7 empty] | 17.5043 | [10 empty] | 77.34%
[9 empty] | 33 | 0 | 17.5043
[9 empty] | 34 | 1 | 17.6708

## Kirjasto (maat) (hidden)
Kirjasto (maat)
Kielivalinta: |  | 1. SUOMI | 2. ENGLANTI | 3. RUOTSI | 4. SAKSA | 5. PUOLA | 6. VIRO | 7. LATVIA | 8. LIETTUA
2 | 1 | Suomi | Finland | Finland | Finnland
| 2 | Viro | Estonia | Estland | Estland
| 3 | Norja | Norway | Norge | Norwegen
| 4 | Tanska | Denmark | Danmark | Dänemark
| 5 | Puola | Poland | Polen | Polen
| 6 | Saksa | Germany | Tyskland | Deutschland
| 7 | Islanti | Iceland | Island | Island
| 8 | Romania | Romania | Rumänien | Rumänien
| 9 | Latvia | Latvia | Lettland | Lettland
| 10 | Liettua | Lithuania | Litauen | Litauen
| 11 | Ruotsi | Sweden | Sverige | Schweden
12
13
14
15
16
17
18
19
20
21
22
23
24
| 25 | Ruotsi | Sweden | Sverige | Schweden

## Kirjasto (kaupungit) (hidden)
Kirjasto (kaupungit)
Kielivalinta: |  | 1. SUOMI | 2. ENGLANTI | 3. RUOTSI | 4. SAKSA | 5. PUOLA | 6. VIRO | 7. LATVIA | 8. LIETTUA
2 | 1 | I (Vantaa) | I (Vantaa) | I (Vanda) | I (Vantaa) | I (Vantaa) | I (Vantaa) | I (Vantaa) | I (Vantaa)
| 2 | II (Jokioinen) | II (Jokioinen) | II (Jockis) | II (Jokioinen) | II (Jokioinen) | II (Jokioinen) | II (Jokioinen) | II (Jokioinen)
| 3 | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä)
| 4 | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä)
| 5 | Tukholma | SWE - Stockholm | SWE - Stockholm | SWE - Stockholm | SWE - Sztokholm | SWE - Stockholm | SWE - Stokholma | SWE - Stokholmas
| 6 | Göteborg | SWE - Gothenburg | SWE - Göteborg | SWE - Göteborg | SWE - Goteborg | SWE - Göteborg | SWE - Gēteborga | SWE - Geteborgas
| 7 | Tallinna | EST - Tallinn | EST - Tallinn | EST - Tallinn | EST - Tallin | EST - Tallinn | EST - Tallina | EST - Talinas
| 8 | Riika | LAT - Riga | LAT - Riga | LAT - Riga | LAT - Ryga | LAT - Riia | LAT - Rīga | LAT - Ryga
| 9 | Vilna | LTU - Vilnius | LTU - Vilnius | LTU - Wilna | LTU - Wilno | LTU - Vilnius | LTU - Viļņa | LTU - Vilnius
| 10 | Varsova | POL - Warsaw | POL - Warszawa | POL - Warschau | POL - Warszawa | POL - Varssavi | POL - Varšava | POL - Varšuva
| 11 | Krakova | POL - Krakow | POL - Krakow | POL - Krakau | POL - Kraków | POL - Kraków | POL - Krakova | POL - Krokuva
| 12 | Gdansk | POL - Gdansk | POL - Gdansk | POL - Danzig | POL - Gdańsk | POL - Gdańsk | POL - Gdaņska | POL - Gdanskas
| 13 | Reykjavík | ISL - Reykjavík | ISL - Reykjavík | ISL - Reykjavík | ISL - Reykjavik | ISL - Reykjavík | ISL - Reikjavīka | ISL - Reikjavikas
| 14 | Bukarest | ROU - Bucharest | ROU - Bukarest | ROU - Bukarest | ROU - Bukareszt | ROU - Bukarest | ROU - Bukareste | ROU - Bukareštas
| 15 | Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslas
| 16 | Kööpenhamina | DEN - Copenhagen | DEN - Köpenhamn | DEN - Kopenhagen | DEN - Kopenhaga | DEN - Kopenhaagen | DEN - Kopenhāgena | DEN - Kopenhaga
| 17 | Berliini | GER - Berlin | GER - Berlin | GER - Berlin | GER - Berlin | GER - Berliin | GER - Berlīne | GER - Berlynas
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
701
702
703
704
705
706
707
708
709
710
711
712
713
714
715
716
717
718
719
720
721
722
723
724
725
726
727
728
729
730
731
732
733
734
735
736
737
738
739
740
741
742
743
744
745
746
747
748
749
750
751
752
753
754
755
756
757
758
759
760
761
762
763
764
765
766
767
768
769
770
771
772
773
774
775
776
777
778
779
780
781
782
783
784
785
786
787
788
789
790
791
792
793
794
795
796
797
798
799
800
801
802
803
804
805
806
807
808
809
810
811
812
813
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
838
839
840
841
842
843
844
845
846
847
848
849
850
851
852
853
854
855
| 856 | Tukholma | Stockholm | Stockholm | Stockholm | Stockholm | Stockholm | Stockholm | Stockholm
| 857 | Malmö | Malmö | Malmö | Malmö | Malmö | Malmö | Malmö | Malmö
| 858 | Göteborg | Gothenburg | Göteborg | Göteborg | Göteborg | Göteborg | Göteborg | Göteborg

## Syötä maat KIRJASTOLINKIT! (hidden)
Syötä maat KIRJASTOLINKIT!
MAA 1 | Finland
MAA 2
MAA 3
MAA 4 |  | Huom oli ennen v.5.7 päivitystä näin:
MAA 5
MAA 6
MAA 7
MAA 8
MAA 9
MAA 10
MAA 11
MAA 12
MAA 13
MAA 14
MAA 15
MAA 16
MAA 17
MAA 18
MAA 19
MAA 20
MAA 21
MAA 22
MAA 23
MAA 24
MAA 25
Syötä maat/valtiot niin, että väliin ei jää tyhjiä rivejä.
Käytettävä kaavaa, joka hakee arvot taulukosta: Kirjasto (maat)

## Syötä kaupungit KIRJASTOLINKIT! (hidden)
Syötä kaupungit KIRJASTOLINKIT! | Finland | MAA 2 | MAA 3 | MAA 4 | MAA 5 | MAA 6 | MAA 7 | MAA 8 | MAA 9 | MAA 10 | MAA 11 | MAA 12 | MAA 13 | MAA 14 | MAA 15 | MAA 16 | MAA 17 | MAA 18 | MAA 19 | MAA 20 | MAA 21 | MAA 22 | MAA 23 | MAA 24 | MAA 22
ALUE 1 | I (Vantaa) | SWE - Stockholm | SWE - Gothenburg | EST - Tallinn | LAT - Riga | LTU - Vilnius | POL - Warsaw | Riga
ALUE 2 | II (Jokioinen)
ALUE 3 | III (Jyväskylä)
ALUE 4 | IV (Sodankylä)
ALUE 5
ALUE 6
ALUE 7
ALUE 8
ALUE 9
ALUE 10
ALUE 11
ALUE 12
ALUE 13
ALUE 14
ALUE 15
ALUE 16
ALUE 17
ALUE 18
ALUE 19
ALUE 20
ALUE 21
ALUE 22
ALUE 23
ALUE 24
ALUE 25
ALUE 26
ALUE 27
ALUE 28
ALUE 29
ALUE 30
ALUE 31
ALUE 32
ALUE 33
ALUE 34
ALUE 35
ALUE 36
ALUE 37
ALUE 38
ALUE 39
Syötä alueet/kaupungit niin, että väliin ei jää tyhjiä rivejä.
Käytettävä kaavaa, joka hakee arvot taulukosta: Kirjasto (kaupungit)

## Syötä pysyvyyskäyrät (hidden)
Syötä pysyvyyskäyrät
| Finland | I (Vantaa) | II (Jokioinen) | III (Jyväskylä) | IV (Sodankylä) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -40 | 0 | 0 | 0 | 0
| -39 | 0 | 0 | 0 | 0
| -38 | 0 | 0 | 0 | 0.00034247
| -37 | 0 | 0 | 0 | 0.00057078
| -36 | 0 | 0 | 0 | 0.0011416
| -35 | 0 | 0 | 0 | 0.0018265
| -34 | 0 | 0 | 0 | 0.002968
| -33 | 0 | 0 | 0 | 0.0041096
| -32 | 0 | 0 | 0 | 0.0047945
| -31 | 0 | 0 | 0.00022831 | 0.0060502
| -30 | 0 | 0 | 0.00034247 | 0.0079909
| -29 | 0 | 0 | 0.00045662 | 0.011187
| -28 | 0 | 0 | 0.00091324 | 0.014726
| -27 | 0 | 0 | 0.0018265 | 0.019064
| -26 | 0 | 0.00034247 | 0.0026256 | 0.022489
| -25 | 0 | 0.00091324 | 0.0038813 | 0.027397
| -24 | 0.00011416 | 0.0013699 | 0.0058219 | 0.030936
| -23 | 0.00034247 | 0.0023973 | 0.0073059 | 0.034018
| -22 | 0.00057078 | 0.002968 | 0.0083333 | 0.041096
| -21 | 0.0011416 | 0.0045662 | 0.010616 | 0.048059
| -20 | 0.0028539 | 0.0058219 | 0.012671 | 0.055251
| -19 | 0.0053653 | 0.0077626 | 0.016553 | 0.062557
| -18 | 0.0070776 | 0.010046 | 0.01895 | 0.068037
| -17 | 0.0092466 | 0.013128 | 0.023288 | 0.074543
| -16 | 0.011872 | 0.018265 | 0.028539 | 0.081621
| -15 | 0.016324 | 0.023288 | 0.035845 | 0.090982
| -14 | 0.021918 | 0.029795 | 0.043493 | 0.10422
| -13 | 0.028653 | 0.03653 | 0.051598 | 0.11747
| -12 | 0.034589 | 0.041324 | 0.060959 | 0.13345
| -11 | 0.040639 | 0.048402 | 0.071575 | 0.15137
| -10 | 0.046575 | 0.056963 | 0.083105 | 0.16861
| -9 | 0.05468 | 0.067352 | 0.097945 | 0.1863
| -8 | 0.063356 | 0.076256 | 0.11667 | 0.20091
| -7 | 0.075 | 0.087785 | 0.13699 | 0.22237
| -6 | 0.08847 | 0.10217 | 0.16096 | 0.24121
| -5 | 0.10548 | 0.12317 | 0.18801 | 0.2718
| -4 | 0.12888 | 0.14452 | 0.21393 | 0.30651
| -3 | 0.15571 | 0.16849 | 0.24406 | 0.34178
| -2 | 0.18425 | 0.19338 | 0.27728 | 0.37648
| -1 | 0.20925 | 0.2234 | 0.3121 | 0.41678
| 0 | 0.2492 | 0.27089 | 0.36792 | 0.46027
| 1 | 0.30993 | 0.34224 | 0.41005 | 0.51119
| 2 | 0.36918 | 0.40137 | 0.45171 | 0.54372
| 3 | 0.41598 | 0.44018 | 0.48653 | 0.57363
| 4 | 0.4508 | 0.47717 | 0.51838 | 0.61016
| 5 | 0.48413 | 0.50776 | 0.54886 | 0.63642
| 6 | 0.51587 | 0.54167 | 0.58139 | 0.66416
| 7 | 0.55331 | 0.58744 | 0.60719 | 0.69053
| 8 | 0.58984 | 0.62123 | 0.63162 | 0.71872
| 9 | 0.61747 | 0.654 | 0.66233 | 0.74886
| 10 | 0.64395 | 0.68836 | 0.69623 | 0.78527
| 11 | 0.67626 | 0.72169 | 0.73105 | 0.82283
| 12 | 0.71416 | 0.75297 | 0.76781 | 0.85114
| 13 | 0.75434 | 0.78493 | 0.80594 | 0.87603
| 14 | 0.78733 | 0.81975 | 0.84509 | 0.89578
| 15 | 0.82626 | 0.85468 | 0.87568 | 0.91804
| 16 | 0.86187 | 0.88059 | 0.89909 | 0.9355
| 17 | 0.88995 | 0.90388 | 0.921 | 0.95274
| 18 | 0.91358 | 0.9226 | 0.93893 | 0.96712
| 19 | 0.93219 | 0.93836 | 0.95491 | 0.97603
| 20 | 0.94783 | 0.95491 | 0.96701 | 0.98265
| 21 | 0.96324 | 0.96758 | 0.97808 | 0.9879
| 22 | 0.97283 | 0.97751 | 0.98653 | 0.99167
| 23 | 0.98082 | 0.98539 | 0.99304 | 0.99498
| 24 | 0.9855 | 0.99098 | 0.9976 | 0.99749
| 25 | 0.9895 | 0.99521 | 0.9992 | 0.99852
| 26 | 0.99372 | 0.99692 | 0.99966 | 0.99954
| 27 | 0.99669 | 0.9984 | 1 | 1
| 28 | 0.99874 | 0.9992 | 1 | 1
| 29 | 0.99966 | 0.99977 | 1 | 1
| 30 | 1 | 1 | 1 | 1
| 31 | 1 | 1 | 1 | 1
| 32 | 1 | 1 | 1 | 1
| 33 | 1 | 1 | 1 | 1
| 34 | 1 | 1 | 1 | 1
| 35 | 1 | 1 | 1 | 1
| 36 | 1 | 1 | 1 | 1
| 37 | 1 | 1 | 1 | 1
| 38 | 1 | 1 | 1 | 1
| 39 | 1 | 1 | 1 | 1
| 40 | 1 | 1 | 1 | 1
| MAA 2 | SWE - Stockholm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0.00022831
| -16 | 0.0012557
| -15 | 0.0047945
| -14 | 0.0068493
| -13 | 0.012557
| -12 | 0.019749
| -11 | 0.029224
| -10 | 0.040297
| -9 | 0.048744
| -8 | 0.062557
| -7 | 0.084475
| -6 | 0.10616
| -5 | 0.13071
| -4 | 0.14772
| -3 | 0.1734
| -2 | 0.20468
| -1 | 0.23185
| 0 | 0.27363
| 1 | 0.30491
| 2 | 0.36507
| 3 | 0.40559
| 4 | 0.45342
| 5 | 0.49874
| 6 | 0.5161
| 7 | 0.55011
| 8 | 0.58858
| 9 | 0.62055
| 10 | 0.65936
| 11 | 0.68094
| 12 | 0.71861
| 13 | 0.76404
| 14 | 0.80936
| 15 | 0.84532
| 16 | 0.86313
| 17 | 0.8895
| 18 | 0.91461
| 19 | 0.93642
| 20 | 0.954
| 21 | 0.96107
| 22 | 0.97306
| 23 | 0.98265
| 24 | 0.99041
| 25 | 0.99566
| 26 | 0.99817
| 27 | 0.9992
| 28 | 1
| 29 | 1
| 30 | 1
| 31 | 1
| 32 | 1
| 33 | 1
| 34 | 1
| 35 | 1
| 36 | 1
| 37 | 1
| 38 | 1
| 39 | 1
| 40 | 1
| MAA 3 | SWE - Gothenburg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0.00045662
| -17 | 0.0018265
| -16 | 0.0037671
| -15 | 0.0063927
| -14 | 0.0074201
| -13 | 0.011301
| -12 | 0.014041
| -11 | 0.018721
| -10 | 0.021233
| -9 | 0.023174
| -8 | 0.030365
| -7 | 0.039041
| -6 | 0.053539
| -5 | 0.074543
| -4 | 0.086872
| -3 | 0.11781
| -2 | 0.16244
| -1 | 0.21119
| 0 | 0.25753
| 1 | 0.28151
| 2 | 0.3355
| 3 | 0.38824
| 4 | 0.44189
| 5 | 0.48162
| 6 | 0.49772
| 7 | 0.53231
| 8 | 0.56667
| 9 | 0.60137
| 10 | 0.64578
| 11 | 0.67169
| 12 | 0.72568
| 13 | 0.7758
| 14 | 0.82249
| 15 | 0.8613
| 16 | 0.88299
| 17 | 0.91781
| 18 | 0.94509
| 19 | 0.9637
| 20 | 0.9766
| 21 | 0.98174
| 22 | 0.98847
| 23 | 0.99372
| 24 | 0.99635
| 25 | 0.9984
| 26 | 0.99909
| 27 | 0.99966
| 28 | 1
| 29 | 1
| 30 | 1
| 31 | 1
| 32 | 1
| 33 | 1
| 34 | 1
| 35 | 1
| 36 | 1
| 37 | 1
| 38 | 1
| 39 | 1
| 40 | 1
| MAA 4 | EST - Tallinn | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0.0025114
| -9 | 0.0030822
| -8 | 0.0050228
| -7 | 0.0086758
| -6 | 0.014041
| -5 | 0.020662
| -4 | 0.028767
| -3 | 0.044292
| -2 | 0.071689
| -1 | 0.10148
| 0 | 0.14212
| 1 | 0.1637
| 2 | 0.20742
| 3 | 0.26221
| 4 | 0.31358
| 5 | 0.36598
| 6 | 0.39087
| 7 | 0.44315
| 8 | 0.49167
| 9 | 0.54167
| 10 | 0.59041
| 11 | 0.6129
| 12 | 0.6589
| 13 | 0.70742
| 14 | 0.75582
| 15 | 0.79966
| 16 | 0.82386
| 17 | 0.86336
| 18 | 0.89874
| 19 | 0.92626
| 20 | 0.94806
| 21 | 0.95913
| 22 | 0.97454
| 23 | 0.98562
| 24 | 0.99258
| 25 | 0.99589
| 26 | 0.99715
| 27 | 0.99886
| 28 | 0.99966
| 29 | 1
| 30 | 1
| 31 | 1
| 32 | 1
| 33 | 1
| 34 | 1
| 35 | 1
| 36 | 1
| 37 | 1
| 38 | 1
| 39 | 1
| 40 | 1
| MAA 5 | LAT - Riga | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0.00034247
| -17 | 0.0010274
| -16 | 0.0020548
| -15 | 0.0037671
| -14 | 0.0047945
| -13 | 0.0067352
| -12 | 0.0097032
| -11 | 0.013356
| -10 | 0.018037
| -9 | 0.020548
| -8 | 0.025228
| -7 | 0.034018
| -6 | 0.049087
| -5 | 0.069977
| -4 | 0.083447
| -3 | 0.1153
| -2 | 0.15377
| -1 | 0.19121
| 0 | 0.22979
| 1 | 0.24521
| 2 | 0.27717
| 3 | 0.31324
| 4 | 0.3476
| 5 | 0.38368
| 6 | 0.40742
| 7 | 0.44806
| 8 | 0.48413
| 9 | 0.52466
| 10 | 0.56393
| 11 | 0.58425
| 12 | 0.62785
| 13 | 0.66998
| 14 | 0.71792
| 15 | 0.7621
| 16 | 0.78048
| 17 | 0.82352
| 18 | 0.86461
| 19 | 0.89452
| 20 | 0.92123
| 21 | 0.93288
| 22 | 0.95091
| 23 | 0.96712
| 24 | 0.9782
| 25 | 0.98733
| 26 | 0.99018
| 27 | 0.99543
| 28 | 0.9976
| 29 | 0.9992
| 30 | 1
| 31 | 1
| 32 | 1
| 33 | 1
| 34 | 1
| 35 | 1
| 36 | 1
| 37 | 1
| 38 | 1
| 39 | 1
| 40 | 1
| MAA 6 | LTU - Vilnius | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0.00011416
| -14 | 0.00068493
| -13 | 0.0015982
| -12 | 0.0037671
| -11 | 0.0054795
| -10 | 0.008105
| -9 | 0.0092466
| -8 | 0.012785
| -7 | 0.016553
| -6 | 0.021804
| -5 | 0.028767
| -4 | 0.03516
| -3 | 0.048858
| -2 | 0.066324
| -1 | 0.10091
| 0 | 0.13904
| 1 | 0.16233
| 2 | 0.19806
| 3 | 0.24201
| 4 | 0.29486
| 5 | 0.34167
| 6 | 0.36553
| 7 | 0.41495
| 8 | 0.45879
| 9 | 0.50377
| 10 | 0.54909
| 11 | 0.57066
| 12 | 0.61963
| 13 | 0.67043
| 14 | 0.72329
| 15 | 0.77203
| 16 | 0.79349
| 17 | 0.83253
| 18 | 0.86906
| 19 | 0.9032
| 20 | 0.92842
| 21 | 0.93973
| 22 | 0.95685
| 23 | 0.96986
| 24 | 0.98037
| 25 | 0.9871
| 26 | 0.99075
| 27 | 0.99429
| 28 | 0.99658
| 29 | 0.99886
| 30 | 0.99989
| 31 | 1
| 32 | 1
| 33 | 1
| 34 | 1
| 35 | 1
| 36 | 1
| 37 | 1
| 38 | 1
| 39 | 1
| 40 | 1
| MAA 7 | POL - Warsaw | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0.0012557
| -10 | 0.003653
| -9 | 0.0047945
| -8 | 0.0090183
| -7 | 0.013356
| -6 | 0.022717
| -5 | 0.041895
| -4 | 0.049429
| -3 | 0.078539
| -2 | 0.11724
| -1 | 0.15571
| 0 | 0.20274
| 1 | 0.23379
| 2 | 0.29498
| 3 | 0.35856
| 4 | 0.41587
| 5 | 0.48139
| 6 | 0.51941
| 7 | 0.59178
| 8 | 0.66039
| 9 | 0.73002
| 10 | 0.79886
| 11 | 0.83482
| 12 | 0.89909
| 13 | 0.94418
| 14 | 0.97648
| 15 | 0.99235
| 16 | 0.99509
| 17 | 0.9984
| 18 | 1
| 19 | 1
| 20 | 1
| 21 | 1
| 22 | 1
| 23 | 1
| 24 | 1
| 25 | 1
| 26 | 1
| 27 | 1
| 28 | 1
| 29 | 1
| 30 | 1
| 31 | 1
| 32 | 1
| 33 | 1
| 34 | 1
| 35 | 1
| 36 | 1
| 37 | 1
| 38 | 1
| 39 | 1
| 40 | 1
| MAA 8 | Riga | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40
-39
-38
-37
-36
-35
-34
-33
-32
-31
-30
-29
-28
-27
-26
-25
-24
-23
-22
-21
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10
-9
-8
-7
-6
-5
-4
-3
-2
-1
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
| MAA 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40
-39
-38
-37
-36
-35
-34
-33
-32
-31
-30
-29
-28
-27
-26
-25
-24
-23
-22
-21
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10
-9
-8
-7
-6
-5
-4
-3
-2
-1
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
| MAA 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40
-39
-38
-37
-36
-35
-34
-33
-32
-31
-30
-29
-28
-27
-26
-25
-24
-23
-22
-21
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10
-9
-8
-7
-6
-5
-4
-3
-2
-1
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
| MAA 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40
-39
-38
-37
-36
-35
-34
-33
-32
-31
-30
-29
-28
-27
-26
-25
-24
-23
-22
-21
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10
-9
-8
-7
-6
-5
-4
-3
-2
-1
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40

## Laskenta vesipatteri 350 (hidden)
|  |  |  | Syötettävät tiedot |  |  | Reynolds-luvun vaikutus korjattavaan lämpötilaeroon
|  |  |  | Tilavuusvirta | 25 | dm3/s
|  |  |  | Tarvittava teho | 570 | W | Tilavuusvirta | Reynolds | Korjaus lämpötilaeroon
|  |  |  | Patterille tulevan ilman lämpötila | 1 | °C | 50 | 4388.9688 | 0.29667
|  |  |  | Patterilta lähtevän ilman lämpötila | 20 | °C | 50 | 5309.2365 | -0.47043
|  |  |  | Menoveden lämpötila | 50 | °C | 50 | 8494.7784 | 0.72366
|  |  |  | Paluuveden lämpötila | 30 | °C | 50 | 4388.9688 | 0.29667 | Korjaus | 0.3
|  |  |  | Arvio Reynolds-luvusta | 1210.5059 | - | 50 | 3964.2299 | 0.41312
|  |  |  | Tarvittava lämpötilaero patterilla | 6.767 | K | 50 | 3539.491 | -0.47043
[7 empty] | 50 | 3114.7521 | -0.85398
|  |  |  | Patterimitoitus menoveden lämpötilan mukaan |  |  | 100 | 7078.982 | 0.8965
|  |  |  | Menoveden lämpötila | 50 | °C | 100 | 8707.1479 | 0.61513
Virhetilanne |  | TRUE | FALSE | Paluuveden lämpötila | -15.4661 | °C | 100 | 13591.6455 | 0.83376
|  | FALSE |  | Virtaama | 0.00208 | dm3/s | 100 | 3822.6503 | -4.9373 | Korjaus | -4.5
|  | FALSE |  | Painehäviö | 0.010445 | kPa | 100 | 7078.982 | 0.8965
|  | FALSE |  | Painehäviö säätövent (KV=1,00) | 0.0056069 | kPa | 100 | 6512.6635 | 1.1048 | 0.0017873 | -10.939 |  | Korjaus lämpötilaeroon
|  | TRUE |  | Virtausnopeus | 0.016949 | m/s | 100 | 5663.1856 | -0.5828
| VIRHE | TRUE |  | Reynolds | 369.8117 | - | 100 | 4955.2874 | -1.0725 |  |  |  | 0.3
[7 empty] | 200 | 11184.7916 | 1.439
|  |  |  | Patterimitoitus paluuveden lämpötilan mukaan |  |  | 200 | 13804.0149 | 1.3612 |  |  |  | 50 | 0.3
Virhetilanne |  | FALSE | TRUE | Menoveden lämpötila | 4.5339 | °C | 200 | 22511.1628 | 2.7945 |  |  |  | 100 | -4.5
|  | FALSE |  | Paluuveden lämpötila | 30 | °C | 200 | 6158.7144 | -4.3388 | Korjaus | -4.5 |  | 200 | -4.5
|  |  |  | Virtaama | -0.005347 | dm3/s | 200 | 11184.7916 | 1.439 |  |  |  | 300 | -4.5
|  | TRUE |  | Painehäviö | #NUM! | kPa | 200 | 9910.5748 | -0.111 | 0.0011045 | -11.0314
|  | TRUE |  | Painehäviö säätövent (KV=1,00) | 0.037054 | kPa | 200 | 8494.7784 | -2.1666 |  |  |  | -0.014644 | -0.92034
|  | TRUE |  | Virtausnopeus | -0.043572 | m/s | 200 | 7503.7209 | -2.2055
| VIRHE | TRUE |  | Reynolds | -950.6817 | - | 300 | 14299.5437 | 2.5297 |  |  |  | 0.00018332 | -0.079116 | 3.0256
[7 empty] | 300 | 17626.6652 | 2.2719
[7 empty] | 300 | 25909.0742 | -0.20978
[7 empty] | 300 | 7645.3006 | -4.4845 | Korjaus | -4.5
[7 empty] | 300 | 14299.5437 | 2.5297
[7 empty] | 300 | 12175.8491 | -0.93511 | 0.0010014 | -12.3554
[7 empty] | 300 | 10760.0527 | -1.745
[7 empty] | 300 | 9202.6766 | -2.9858
Tarvittavan lämpötilaeron laskenta
[7 empty] | Tilavuusvirta | Kerroin |  | Eksponenttisovite
[7 empty] | 50 | 0.10404 |  | 0.45113 | -4.0233 | 0.017894
[7 empty] | 100 | 0.14328 |  | 0.076448
[7 empty] | 200 | 0.1978
[7 empty] | 300 | 0.23203 |  | 3-asteen polynomin sovite
[10 empty] | 2.331e-09 | -2.4135e-06 | 0.0011061 | 0.054477
0.080657
Nestepuolen painehäviö
[7 empty] | 1.787 | 6.4739 | 648.0329

## KirjastoC (kaupungit) (hidden)
KirjastoC (kaupungit)
Kielivalinta: |  | 1. SUOMI | 2. ENGLANTI | 3. RUOTSI | 4. SAKSA | 5. PUOLA | 6. VIRO | 7. LATVIA | 8. LIETTUA
2 | 1 | I (Vantaa) | I (Vantaa) | I (Vanda) | I (Vantaa) | I (Vantaa) | I (Vantaa) | I (Vantaa) | I (Vantaa)
| 2 | II (Jokioinen) | II (Jokioinen) | II (Jockis) | II (Jokioinen) | II (Jokioinen) | II (Jokioinen) | II (Jokioinen) | II (Jokioinen)
| 3 | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä) | III (Jyväskylä)
| 4 | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä) | IV (Sodankylä)
| 5 | Tukholma | SWE - Stockholm | SWE - Stockholm | SWE - Stockholm | SWE - Sztokholm | SWE - Stockholm | SWE - Stokholma | SWE - Stokholmas
| 6 | Göteborg | SWE - Gothenburg | SWE - Göteborg | SWE - Göteborg | SWE - Goteborg | SWE - Göteborg | SWE - Gēteborga | SWE - Geteborgas
| 7 | Tallinna | EST - Tallinn | EST - Tallinn | EST - Tallinn | EST - Tallin | EST - Tallinn | EST - Tallina | EST - Talinas
| 8 | Riika | LAT - Riga | LAT - Riga | LAT - Riga | LAT - Ryga | LAT - Riia | LAT - Rīga | LAT - Ryga
| 9 | Vilna | LTU - Vilnius | LTU - Vilnius | LTU - Wilna | LTU - Wilno | LTU - Vilnius | LTU - Viļņa | LTU - Vilnius
| 10 | Varsova | POL - Warsaw | POL - Warszawa | POL - Warschau | POL - Warszawa | POL - Varssavi | POL - Varšava | POL - Varšuva
| 11 | Krakova | POL - Krakow | POL - Krakow | POL - Krakau | POL - Kraków | POL - Kraków | POL - Krakova | POL - Krokuva
| 12 | Gdansk | POL - Gdansk | POL - Gdansk | POL - Danzig | POL - Gdańsk | POL - Gdańsk | POL - Gdaņska | POL - Gdanskas
| 13 | Reykjavík | ISL - Reykjavík | ISL - Reykjavík | ISL - Reykjavík | ISL - Reykjavik | ISL - Reykjavík | ISL - Reikjavīka | ISL - Reikjavikas
| 14 | Bukarest | ROU - Bucharest | ROU - Bukarest | ROU - Bukarest | ROU - Bukareszt | ROU - Bukarest | ROU - Bukareste | ROU - Bukareštas
| 15 | Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslo | NOR - Oslas
| 16 | Kööpenhamina | DEN - Copenhagen | DEN - Köpenhamn | DEN - Kopenhagen | DEN - Kopenhaga | DEN - Kopenhaagen | DEN - Kopenhāgena | DEN - Kopenhaga
| 17 | Berliini | GER - Berlin | GER - Berlin | GER - Berlin | GER - Berlin | GER - Berliin | GER - Berlīne | GER - Berlynas
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
701
702
703
704
705
706
707
708
709
710
711
712
713
714
715
716
717
718
719
720
721
722
723
724
725
726
727
728
729
730
731
732
733
734
735
736
737
738
739
740
741
742
743
744
745
746
747
748
749
750
751
752
753
754
755
756
757
758
759
760
761
762
763
764
765
766
767
768
769
770
771
772
773
774
775
776
777
778
779
780
781
782
783
784
785
786
787
788
789
790
791
792
793
794
795
796
797
798
799
800
801
802
803
804
805
806
807
808
809
810
811
812
813
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
838
839
840
841
842
843
844
845
846
847
848
849
850
851
852
853
854
855
| 856 | Tukholma | Stockholm | Stockholm | Stockholm | Stockholm | Stockholm | Stockholm | Stockholm
| 857 | Malmö | Malmö | Malmö | Malmö | Malmö | Malmö | Malmö | Malmö
| 858 | Göteborg | Gothenburg | Göteborg | Göteborg | Göteborg | Göteborg | Göteborg | Göteborg

## C5 Lämmitys (hidden)
LÄMMITYSPATTERI
Patterivaihtoehdot
LÄM-1 | 61 = Water- soveltuu esim. 50/30 vedelle (mitoita ohjelmassa), Vakiotoimitus mallissa C5 Water jos ei muuta pyydetty | [8 empty] | 50/30 |  |  |  | Soveltuva alue |  | Nimellis | Ala | Ylä
LÄM-2 | 62 = Water- matalille lämpötiloille, esim. 35/25 - 35/30 (mitoita ohjelmassa) | [8 empty] | 35/25 - 35/30 |  |  |  | Menovesi |  | 50 | 45 | 55 | Value not applicable
[14 empty] | Paluuvesi |  | 30 | 25 | 35
Valitse lämmityspatteri |  | 1 | [7 empty] | 3
Valittu patteri |  | LÄM-1 | 50/30
Säätöventtiili | Belimo C215Q-J, säätöasento 4 (kv = 1.5) | [7 empty] | TULOSTUKSEEN
Venttiilin kvs | - | [7 empty] | Ohjeteksti |  | The selected coil model is suitable for heating water ~50/30 | [5 empty] | The selected coil model is suitable for heating water ~50/30 | The selected coil model is suitable for heating water ~50/30
[9 empty] | Tarvittava teho |  | 3.9661 | kW |  |  |  |  | 3.9661 | 3.9661
Tilavuusvirta |  | 125 | l/s | Tiheys |  | cp |  |  | Menovesi
TLTO |  | -5 | °C | 1.3171 | kg/m³ | 1004 | J/kgK |  | Paluuvesi
TTULO |  | 20 | °C | 1.2048 | kg/m³ | 1009 | J/kgK
Patterimitoitus menoveden lämpötilan mukaan
Tavoitelämpötilat lämmitysvedelle | [8 empty] | Menoveden lämpötila |  |  |  |  | 50 | ºC |  | 50 | 50
Valitulla patterilla lämmitysvedet n.50/30 | [8 empty] | Paluuveden lämpötila |  |  |  |  | 30.9637 | ºC |  | 30.9637 | 30.9637
TMENOVESI |  | 50 | °C |  | dT | 32.5 |  |  | Virtaama |  |  |  |  | 0.049771 | dm3/s |  | 0.049771 | 0.049771
TPALUUVESI |  | 30 | °C |  | log | 32.5 |  |  | Patterin nestepuolen painehäviö |  |  |  |  | 0.45463 | kPa |  | 0.45463 | 0.45463
[9 empty] | Säätöventtiilin painehäviö* |  |  |  |  | - | kPa |  | - | -
[9 empty] | Virtausnopeus |  |  |  |  | 0.16366 | m/s |  | 0.16366 | 0.16366
Tehontarve |  | 3.9661 | kW
Tarvittava dT |  | 32.9818 | K | [5 empty] | Patterimitoitus paluuveden lämpötilan mukaan
[9 empty] | Menoveden lämpötila |  |  |  |  | - | ºC |  | 50.9637 | -
Mitoitus menoveden lämpötilan mukaan |  |  |  |  | Mitoitus paluuveden lämpötilan mukaan |  |  |  | Paluuveden lämpötila |  |  |  |  | - | ºC |  | 30 | -
TPALUUVESI |  | 30.9637 | °C |  | TMENOVESI |  | 50.9637 | °C | Virtaama |  |  |  |  | - | dm3/s |  | 0.045195 | -
Virtaama |  | 0.049771 | l/s |  | Virtaama |  | 0.045195 | l/s | Patterin nestepuolen painehäviö |  |  |  |  | - | kPa |  | 0.37574 | -
Patterin nestepuolen painehäviö |  | 0.45463 | kPa |  | Patterin nestepuolen painehäviö |  | 0.37574 | kPa | Säätöventtiilin painehäviö* |  |  |  |  | - | kPa |  | - | -
Säätöventtiilin painehäviö |  | - | kPa |  | Säätöventtiilin painehäviö |  | - |  | Virtausnopeus |  |  |  |  | - | m/s |  | 0.14862 | -
| Kvs tarkistus | #VALUE! | [6 empty] | Value out of range. Check input parameters. |  |  |  |  | Value out of range. Check input parameters. |  |  | Value out of range. Check input parameters. | Value out of range. Check input parameters.
Reynolds-luvun laskenta |  |  |  |  | Reynolds-luvun laskenta |  |  |  | * No control valve or actuator / heating group selected. |  |  |  |  | * No control valve or actuator / heating group selected. |  |  | * No control valve or actuator / heating group selected. | * No control valve or actuator / heating group selected.
Jakotukista |  | 5 | kpl |  | Jakotukista |  | 5 | kpl
Virtaama, jakautunut |  | 0.0099543 | l/s |  | Virtaama, jakautunut |  | 0.0090391 | l/s
Putken sisähalkaisija |  | 8.8 | mm |  | Putken sisähalkaisija |  | 8.8 | mm | Ilmapuolen painehäviö |  |  |  | 1.6108 | Pa
Virtausnopeus |  | 0.16366 | m/s |  | Virtausnopeus |  | 0.14862 | m/s | Muutos mitattuun konstruktioon |  |  |  | 0 | Pa
Reynolds-luku |  | 2057.493 |  |  | Reynolds-luku |  | 1868.3286
Tarkastuksen ehtoja
Maksimivirtaus |  | 2 | l/s
Maksimipainehäviö |  | 60 | kPa
Reynolds-luvun minimi |  | 2000
Versiosta v7.1 alkaen
Tarkastukset |  |  |  |  | Tarkastukset |  |  |  | Säätöventtiilin valinta ja vaikutukset tulostukseen (v7.1 sähköposti 20.1.2025 mukaisesti)
Valittu vesipatteri |  | TRUE |  |  | Valittu vesipatteri |  | TRUE
Virtaama alle maksimivirtauksen |  | TRUE |  |  | Virtaama alle maksimivirtauksen |  | TRUE |  | * No control valve or actuator / heating group selected.
Menovesi ei soveltuva |  | TRUE |  |  | Paluuvesi ei soveltuva |  | TRUE |  | * Included in the delivery: 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (kvs = 1.5).
Painehäviö alle maksimin |  | TRUE |  |  | Painehäviö alle maksimin |  | TRUE |  | * Included in the delivery: Post-heating pump unit for 50/30, assembled and insulated (kvs = 1.5).
Reynolds yli minimin |  | TRUE |  |  | Reynolds yli minimin |  | FALSE |  | * Included in the delivery: 2-way valve and actuator for post-heating, designed for a coil with 35/25 – 35/30 specifications (kvs = 5.7).
Kaikki kunnossa? |  | TRUE |  |  | Kaikki kunnossa? |  | FALSE |  | * Included in the delivery: Post-heating pump unit for 35/25 – 35/30, assembled and insulated (kvs = 5.7).
Valintakoodin valinta
[9 empty] | 3 | 61 = Water – Suitable for, e.g., 50/30 water (dimensioning in the program). Standard delivery for model C5 Water unless otherwise specified.
[9 empty] | 1 | 3 = Water – Actuators or valves for the water coil are not included in the delivery. Standard delivery for C-series Water models unless otherwise specified.
[9 empty] | Patterivalinta: |  | 3
[9 empty] | - | * No control valve or actuator / heating group selected.
[9 empty] | 1.5 | * Included in the delivery: 2-way valve and actuator for post-heating, designed for a coil with 50/30 specifications (kvs = 1.5).
[9 empty] | 1.5 | * Included in the delivery: Post-heating pump unit for 50/30, assembled and insulated (kvs = 1.5).
[9 empty] | Patterivalinta: |  | 4
[9 empty] | - | * No control valve or actuator / heating group selected.
[9 empty] | 5.7 | * Included in the delivery: 2-way valve and actuator for post-heating, designed for a coil with 35/25 – 35/30 specifications (kvs = 5.7).
[9 empty] | 5.7 | * Included in the delivery: Post-heating pump unit for 35/25 – 35/30, assembled and insulated (kvs = 5.7).
Toimilaitevalinta
[9 empty] | Kvs | Malliteksti
[9 empty] | - | * No control valve or actuator / heating group selected.

## C5 Jäähdytys (hidden)
JÄÄHDYTYSPATTERI
Patterivaihtoehdot
JÄ-1 | 1 = Jäähdytys neste, patteriteho 1 ,esim. 7/12 - 10/15 (mitoita ohjelmassa) | [8 empty] | 7/12 |  |  |  | Soveltuva alue |  | Nimellis | Ala | Ylä
JÄ-2 | 2 = Jäähdytys neste , patteriteho 2. esim. 10/18 -kaukokylmä/maajärjestelmä (mitoita ohjelmassa) | [8 empty] | 10/18 |  |  |  | Menovesi |  | 7 | 5 | 11 | Value not applicable
[14 empty] | Paluuvesi |  | 12 | 10 | 16
Valitse lämmityspatteri |  | 1 | [7 empty] | 2
Valittu patteri |  | JÄ-1 | 7/12
Säätöventtiili | Belimo R3015-4P (kvs = 4.0) | [7 empty] | TULOSTUKSEEN
Venttiilin kvs | - | [7 empty] | Ohjeteksti |  | The selected coil model is suitable for cooling water ~7/12 | [5 empty] | The selected coil model is suitable for cooling water ~7/12 | The selected coil model is suitable for cooling water ~7/12
[9 empty] | Tarvittava teho (tuntuva) |  | 1.212 | kW |  |  |  |  | 1.212 | 1.212
Tilavuusvirta |  | 125 | l/s | Tiheys |  | cp |  |  | Latentti teho |  | 0.57564 | kW |  |  |  |  | 0.57564 | 0.57564
TLTO |  | 25 | °C | 1.1846 | kg/m³ | 1010 | J/kgK |  | Kokonaisteho |  | 1.7876 | kW |  |  |  |  | 1.7876 | 1.7876
Kosteus |  | 65 | % | 0.012901 | kg/kg |  |  |  | Menovesi
TTULO |  | 17 | °C | 1.2172 | kg/m³ | 1008.4 | J/kgK |  | Paluuvesi
Kosteus |  | 93.9108 | % | 0.011367 | kg/kg
Tavoitelämpötilat jäähdytysvedelle | [8 empty] | Patterimitoitus menoveden lämpötilan mukaan
Valitulla patterilla jäähdytysvedet n.7/12 | [8 empty] | Menoveden lämpötila |  |  |  |  | - | ºC |  | 7 | -
TMENOVESI |  | 7 | °C |  | dT | -11.5 |  |  | Paluuveden lämpötila |  |  |  |  | - | ºC |  | 21.1426 | -
TPALUUVESI |  | 12 | °C |  | log | -26.1667 |  |  | Virtaama |  |  |  |  | - | dm3/s |  | 0.030195 | -
[9 empty] | Patterin nestepuolen painehäviö |  |  |  |  | - | kPa |  | 0.1244 | -
Kastepiste |  | 17.9523 | °C | [5 empty] | Säätöventtiilin painehäviö* |  |  |  |  | - | kPa |  | - | -
Osuus vesilämpötila-alueesta |  | 219% | Maksimi | 250% |  |  |  |  | Virtausnopeus |  |  |  |  | - | m/s |  | 0.070923 | -
Kosteussisällön lasku (kondensio) |  | 11.89% | [6 empty] | Value out of range. Check input parameters. | [7 empty] | Value out of range. Check input parameters. | Value out of range. Check input parameters.
Patterimitoitus paluuveden lämpötilan mukaan
Tuntuvan tehon tarve |  | 1.212 | kW | [5 empty] | Menoveden lämpötila |  |  |  |  | - | ºC |  | 16.1426 | -
Latentti teho |  | 0.57564 | kW | [5 empty] | Paluuveden lämpötila |  |  |  |  | - | ºC |  | 12 | -
Kokonaistehon tarve |  | 1.7876 | kW | [5 empty] | Virtaama |  |  |  |  | - | dm3/s |  | -0.10309 | -
Tarvittava dT |  | 6.9287 | K | [5 empty] | Patterin nestepuolen painehäviö |  |  |  |  | - | kPa |  | #NUM! | -
[9 empty] | Säätöventtiilin painehäviö* |  |  |  |  | - | kPa |  | - | -
Mitoitus menoveden lämpötilan mukaan |  |  |  |  | Mitoitus paluuveden lämpötilan mukaan |  |  |  | Virtausnopeus |  |  |  |  | - | m/s |  | -0.24213 | -
TPALUUVESI |  | 21.1426 | °C |  | TMENOVESI |  | 16.1426 | °C | Value out of range. Check input parameters. | [7 empty] | Value out of range. Check input parameters. | Value out of range. Check input parameters.
Virtaama |  | 0.030195 | l/s |  | Virtaama |  | -0.10309 | l/s | * No control valve or actuator / cooling group selected. | [7 empty] | * No control valve or actuator / cooling group selected. | * No control valve or actuator / cooling group selected.
Patterin nestepuolen painehäviö |  | 0.1244 | kPa |  | Patterin nestepuolen painehäviö |  | #NUM! | kPa
Säätöventtiilin painehäviö |  | - | kPa |  | Säätöventtiilin painehäviö |  | -
[9 empty] | Ilmapuolen painehäviö |  |  |  | 2.2245 | Pa
Reynolds-luvun laskenta |  |  |  |  | Reynolds-luvun laskenta |  |  |  | Muutos mitattuun konstruktioon |  |  |  | 2.2245 | Pa | Mitattu ilman jäähdytyspatteria
Jakotukista |  | 7 | kpl |  | Jakotukista |  | 7 | kpl
Virtaama, jakautunut |  | 0.0043136 | l/s |  | Virtaama, jakautunut |  | -0.014727 | l/s
Putken sisähalkaisija |  | 8.8 | mm |  | Putken sisähalkaisija |  | 8.8 | mm
Virtausnopeus |  | 0.070923 | m/s |  | Virtausnopeus |  | -0.24213 | m/s
Reynolds-luku |  | 520.104 |  |  | Reynolds-luku |  | -1775.6056
Tarkastuksen ehtoja
Maksimivirtaus |  | 2 | l/s
Maksimipainehäviö |  | 60 | kPa
Reynolds-luvun minimi |  | 1500
Tarkastukset |  |  |  |  | Tarkastukset
Valittu vesipatteri |  | TRUE |  |  | Valittu vesipatteri |  | TRUE
Virtaama alle maksimivirtauksen |  | TRUE |  |  | Virtaama alle maksimivirtauksen |  | TRUE
Menovesi ei soveltuva |  | TRUE |  |  | Paluuvesi ei soveltuva |  | TRUE
Painehäviö alle maksimin |  | TRUE |  |  | Painehäviö alle maksimin |  | FALSE
Reynolds yli minimin |  | FALSE |  |  | Reynolds yli minimin |  | FALSE
Paluuvesi soveltuva |  | TRUE |  |  | Menovesi soveltuva |  | TRUE | Rajoitetaan +5 °C alimmillaan (v7.1 muutospyyntö)
Kaikki kunnossa? |  | FALSE |  |  | Kaikki kunnossa? |  | FALSE
Versiosta v7.1 alkaen
Säätöventtiilin valinta ja vaikutukset tulostukseen (v7.1 sähköposti 20.1.2025 mukaisesti)
* No control valve or actuator / cooling group selected.
* Included in the delivery: 3-way valve and actuator for cooling, designed for a coil with 7/12 – 10/15 specifications (kvs = 4).
* Included in the delivery: Cooling pump unit for 7/12 – 10/15, assembled and insulated (kvs = 4).
* Included in the delivery: 3-way valve and actuator for cooling, designed for a coil with 10/18 specifications (kvs = 2.5).
* Included in the delivery: Cooling pump unit for 10/18, assembled and insulated (kvs = 2.5).
Valintakoodin valinta
[9 empty] | 2 | 1 = Cooling, liquid – Coil capacity 1, e.g., 7/12 – 10/15 (dimensioning in the program). Standard delivery in the C-series if a cooling coil is selected and nothing else is specified.
[9 empty] | 1 | 0 = No cooling actuators or valves. Standard delivery unless otherwise specified.
[9 empty] | Patterivalinta: |  | 2
[9 empty] | - | * No control valve or actuator / cooling group selected.
[9 empty] | 4 | * Included in the delivery: 3-way valve and actuator for cooling, designed for a coil with 7/12 – 10/15 specifications (kvs = 4).
[9 empty] | 4 | * Included in the delivery: Cooling pump unit for 7/12 – 10/15, assembled and insulated (kvs = 4).
[9 empty] | Patterivalinta: |  | 3
[9 empty] | - | * No control valve or actuator / cooling group selected.
[9 empty] | 2.5 | * Included in the delivery: 3-way valve and actuator for cooling, designed for a coil with 10/18 specifications (kvs = 2.5).
[9 empty] | 2.5 | * Included in the delivery: Cooling pump unit for 10/18, assembled and insulated (kvs = 2.5).
Toimilaitevalinta
[9 empty] | Kvs | Malliteksti
[9 empty] | - | * No control valve or actuator / cooling group selected.

## C5 LÄM-1 (hidden)
TARJOUSNUMEROMME 123718-TK
RIVI |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | Mitoituspiste
LUKUMÄÄRÄ | bar: 1 to 11
KOJE | [14 empty] | Tilavuusvirta |  | 125 | l/s | Tiheys |  | cp |  | Ilmapuolen painehäviö |  |  | 1.6108 | Pa
KOJENO | [14 empty] | TLTO |  | -5 | °C | 1.3171 | kg/m³ | 1004 | J/kgK
TYYPPI | [14 empty] | TTULO |  | 20 | °C | 1.2048 | kg/m³ | 1009 | J/kgK
KÄYTTÖ |  | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM
KÄTISYYS | [14 empty] | Tavoitelämpötilat lämmitysvedelle
ASENTO | [14 empty] | TMENOVESI |  | 50 | °C
LAMELLIMATERIAALI | [14 empty] | TPALUUVESI |  | 30 | °C | bar: 1 to 11
KEHYSMATERIAALI | [19 empty] | dT | 32.5 | bar: 1 to 11
LIUOS |  | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | [8 empty] | 32.5
PITOISUUS | % | [13 empty] | Tehontarve |  | 3.9661 | kW
[15 empty] | Tarvittava dT |  | 32.9818 | K
OP.LEVEYS | mm | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
OP.KORKEUS | mm | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  |  | Mitoitus menoveden lämpötilan mukaan |  |  |  |  | Mitoitus paluuveden lämpötilan mukaan
KEH.LEVEYS | mm | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 |  |  | TPALUUVESI |  | 30.9637 | °C |  | TMENOVESI |  | 50.9637 | °C
KEH.KORKEUS | mm | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  |  | Virtaama |  | 0.049771 | l/s |  | Virtaama |  | 0.045195 | l/s
KEH.SYVYYS | mm | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  |  | Painehäviö |  | 0.45463 | kPa |  | Painehäviö |  | 0.37574 | kPa
TEHO | kW | 6 | 9 | 12 | 15 | 18 | 7.2 | 9.6 | 12 | 5.4 | 7.2 | 9 |  |  | Jakotukista |  | 5 | kpl |  | Jakotukista |  | 5 | kpl
ILMAN TILAVUUSVIRTA | m3/s | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 |  |  | Virtaama, jakautunut |  | 0.0099543 | l/s |  | Virtaama, jakautunut |  | 0.0090391 | l/s
ILMAN MASSAVIRTA | kg/s | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 |  |  | Putken sisähalkaisija |  | 8.8 | mm |  | Putken sisähalkaisija |  | 8.8 | mm
TULEVA ILMA | oC | -5 | -5 | -5 | -5 | -5 | 1e-05 | 1e-05 | 1e-05 | 5 | 5 | 5 |  |  | Virtausnopeus |  | 0.16366 | m/s |  | Virtausnopeus |  | 0.14862 | m/s
LÄHTEVÄ ILMA | oC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | Reynolds-luku |  | 2057.493 |  |  | Reynolds-luku |  | 1868.3286
ILMAN NOPEUS | m/s | 0.68 | 1.03 | 1.37 | 1.71 | 2.05 | 1.03 | 1.37 | 1.71 | 1.03 | 1.37 | 1.71
ILMAN PAINEHÄVIÖ | Pa | 3.6 | 7.1 | 11.6 | 17 | 23.1 | 7.1 | 11.6 | 17 | 7.1 | 11.6 | 17 |  |  | qV | dT | P | qW | [5 empty] | dT | qV | P
[15 empty] | 0.5 | 32.4358 | 15 | 0.18 |  | 3.0475 | -7.8899 | 0.00037452 |  | 32.4358 | 0.5 | 15
TULEVA NESTE | oC | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 0.5 | 30 | 12 | 0.14 | [5 empty] | 32.4358 | 0.4 | 12
LÄHTEVÄ NESTE | oC | 30 | 30 | 30 | 30 | 33 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 0.5 | 27.4241 | 9 | 0.11 | [5 empty] | 32.4358 | 0.3 | 9
NESTEVIRTA | l/s | 0.07 | 0.11 | 0.14 | 0.18 | 0.26 | 0.09 | 0.12 | 0.14 | 0.07 | 0.09 | 0.11 | 9.2092
NESTE NOPEUS | m/s | 0.21 | 0.31 | 0.42 | 0.52 | 0.74 | 0.25 | 0.33 | 0.42 | 0.19 | 0.25 | 0.31 |  |  | qV | dT | P | qW | [5 empty] | dT | qV | P
NESTEEN PAINEHÄVIÖ | kPa | 1 | 2.2 | 3.8 | 5.8 | 11.2 | 1.4 | 2.5 | 3.8 | 0.8 | 1.4 | 2.2 |  |  | 0.4 | 32.4358 | 12 | 0.14 |  | 3.0475 | -8.113 | 0.00029962 |  | 30 | 0.5 | 12
PUTKIYHDE | DN | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K |  |  | 0.4 | 30 | 9.6 | 0.12 | [5 empty] | 30 | 0.4 | 9.6
HYÖTYSUHDE | % | 32.5 | 32.5 | 32.5 | 32.5 | 34 | 30 | 30 | 30 | 27.5 | 27.5 | 27.5 |  |  | 0.4 | 27.4241 | 7.2 | 0.09 | [5 empty] | 30 | 0.3 | 7.2
RIVISYYS |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | qV | dT | P | qW | [5 empty] | dT | qV | P
LAMELLIJAKO | mm | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 0.3 | 32.4358 | 9 | 0.11 |  | 3.0475 | -8.4007 | 0.00022471 |  | 27.4241 | 0.5 | 9
NESTETILAVUUS | l | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 |  |  | 0.3 | 30 | 7.2 | 0.09 | [5 empty] | 27.4241 | 0.4 | 7.2
PAINO | kg | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  | 0.3 | 27.4241 | 5.4 | 0.07 | [5 empty] | 27.4241 | 0.3 | 5.4
ERISTYS | sisähalk. | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 |  |  | Mitoitustilavuusvirralla
PISARANEROTIN | jako | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  | qV | dT | P
TIPPUVESIALLAS | l/s jako | 0.014 | 0.022 | 0.028 | 0.036 | 0.052 | 0.018 | 0.024 | 0.028 | 0.014 | 0.018 | 0.022 |  |  | 0.125 | 32.4358 | 3.75 |  |  | 3.0475 | -9.2762 | 9.363e-05
PINNOITUS | m² | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 |  |  | 0.125 | 30 | 3
MAALAUS | m/s | 0.23018 | 0.36172 | 0.46037 | 0.5919 | 0.85496 | 0.29595 | 0.3946 | 0.46037 | 0.23018 | 0.29595 | 0.36172 |  |  | 0.125 | 27.4241 | 2.25
HOPEAPITOISUUS | Reynolds | 2893.7262 | 4547.2841 | 5787.4525 | 7441.0103 | 10748.126 | 3720.5052 | 4960.6736 | 5787.4525 | 2893.7262 | 3720.5052 | 4547.2841
JÄÄT.SUOJAMUHVEJA | kpl
Tuotekoodit ja huomautukset per positio
1. EC-HEAT-650-450-2-2-25K-5-R-9.52
Huom:
2. EC-HEAT-650-450-2-2-25K-5-R-9.52
Huom:
3. EC-HEAT-650-450-2-2-25K-5-R-9.52
Huom:
4. EC-HEAT-650-450-2-2-25K-5-R-9.52
Huom:
Tulevan ilman tiheys | kg/m³ | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.293 | 1.293 | 1.293 | 1.2698 | 1.2698 | 1.2698
lähtevän ilman tiheys | kg/m³ | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048
Logaritminen ylilämpötila | K | 32.4358 | 32.4358 | 32.4358 | 32.4358 | 33.8426 | 30 | 30 | 30 | 27.4241 | 27.4241 | 27.4241
Aritmeettinen dT | K | 32.5 | 32.5 | 32.5 | 32.5 | 34 | 30 | 30 | 30 | 27.5 | 27.5 | 27.5
[14 empty] | 1.6981 | 4.0079 | 55.0293
[16 empty] | 1.9762 | 5.1409 | 170.8665

## C5 LÄM-2 (hidden)
TARJOUSNUMEROMME 123720-TK
RIVI |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | Mitoituspiste
LUKUMÄÄRÄ | bar: 1 to 11
KOJE | [14 empty] | Tilavuusvirta |  | 125 | l/s | Tiheys |  | cp |  | Ilmapuolen painehäviö |  |  | 2.591 | Pa
KOJENO | [14 empty] | TLTO |  | -5 | °C | 1.3171 | kg/m³ | 1004 | J/kgK
TYYPPI | [14 empty] | TTULO |  | 20 | °C | 1.2048 | kg/m³ | 1009 | J/kgK
KÄYTTÖ |  | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM | LÄMM
KÄTISYYS | [14 empty] | Tavoitelämpötilat lämmitysvedelle
ASENTO | [14 empty] | TMENOVESI |  | 50 | °C
LAMELLIMATERIAALI | [14 empty] | TPALUUVESI |  | 30 | °C | bar: 1 to 11
KEHYSMATERIAALI | [19 empty] | dT | 32.5 | bar: 1 to 11
LIUOS |  | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | [8 empty] | 22.1284
PITOISUUS | % | [13 empty] | Tehontarve |  | 3.9661 | kW |  |  | 22.1284
[15 empty] | Tarvittava dT |  | 22.1284 | K
OP.LEVEYS | mm | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
OP.KORKEUS | mm | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  |  | Mitoitus menoveden lämpötilan mukaan |  |  |  |  | Mitoitus paluuveden lämpötilan mukaan
KEH.LEVEYS | mm | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 |  |  | TPALUUVESI |  | 9.2568 | °C |  | TMENOVESI |  | 29.2568 | °C
KEH.KORKEUS | mm | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  |  | Virtaama |  | 0.023254 | l/s |  | Virtaama |  | -1.2748 | l/s
KEH.SYVYYS | mm | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  |  | Painehäviö |  | 0.011631 | kPa |  | Painehäviö |  | #NUM! | kPa
[16 empty] | dT | 22.1284 |  |  |  | dT | 22.1284
TEHO | kW | 6 | 9 | 12 | 15 | 18 | 9 | 12 | 15 | 5.4 | 7.2 | 9
ILMAN TILAVUUSVIRTA | m3/s | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 |  |  | Jakotukista |  | 13 | kpl |  | Jakotukista |  | 13 | kpl
ILMAN MASSAVIRTA | kg/s | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 |  |  | Virtaama, jakautunut |  | 0.0017888 | m/s |  | Virtaama, jakautunut |  | -0.098059 | m/s
TULEVA ILMA | oC | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | 5 | 5 | 5 |  |  | Putken sisähalkaisija |  | 8.8 | mm |  | Putken sisähalkaisija |  | 8.8 | mm
LÄHTEVÄ ILMA | oC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | Virtausnopeus |  | 0.029411 | m/s |  | Virtausnopeus |  | -1.6122 | m/s
ILMAN NOPEUS | m/s | 0.68 | 1.03 | 1.37 | 1.71 | 2.05 | 1.03 | 1.37 | 1.71 | 1.03 | 1.37 | 1.71 |  |  | Reynolds-luku |  | 369.7363 |  |  | Reynolds-luku |  | -20268.2126
ILMAN PAINEHÄVIÖ | Pa | 5.7 | 11.2 | 18.2 | 26.6 | 36.1 | 11.2 | 18.2 | 26.6 | 11.2 | 18.2 | 25.5
[15 empty] | qV | dT | P | qW | [5 empty] | dT | qV | P
TULEVA NESTE | oC | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 0.5 | 25 | 15 | 0.72 |  | 1.6037 | -2.3848 | 0.092108 |  | 25 | 0.5 | 16.0735
LÄHTEVÄ NESTE | oC | 25 | 25 | 25 | 25 | 26.5 | 27 | 30 | 30 | 25.5 | 25 | 25.5 |  |  | 0.5 | 22.5 | 15 | 0.36 | [5 empty] | 25 | 0.4 | 12.8333
NESTEVIRTA | l/s | 0.14 | 0.22 | 0.29 | 0.36 | 0.51 | 0.27 | 0.58 | 0.72 | 0.14 | 0.17 | 0.23 | 9.1464 |  | 0.5 | 17.75 | 9 | 0.23 | [5 empty] | 25 | 0.3 | 10.5411
NESTE NOPEUS | m/s | 0.16 | 0.24 | 0.32 | 0.4 | 0.56 | 0.3 | 0.64 | 0.8 | 0.15 | 0.19 | 0.25
NESTEEN PAINEHÄVIÖ | kPa | 0.3 | 0.8 | 1.3 | 2 | 3.9 | 1.2 | 5 | 7.6 | 0.3 | 0.7 | 0.9 |  |  | qV | dT | P | qW | [5 empty] | dT | qV | P
PUTKIYHDE | DN | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K |  |  | 0.4 | 22.5 | 12 | 0.29 |  | 1.5415 | -2.4099 | 0.089828 |  | 22.5 | 0.5 | 13.5748
HYÖTYSUHDE | % | [13 empty] | 0.4 | 25 | 12 | 0.58 | [5 empty] | 22.5 | 0.4 | 10.9094
[15 empty] | 0.4 | 17.5 | 7.2 | 0.17 | [5 empty] | 22.5 | 0.3 | 8.5993
RIVISYYS |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
LAMELLIJAKO | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2 |  |  | qV | dT | P | qW | [5 empty] | dT | qV | P
NESTETILAVUUS | l | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 |  |  | 0.3 | 22.5 | 9 | 0.22 |  | 1.9324 | -3.8648 | 0.020967 |  | 17.5 | 0.5 | 9.072
PAINO | kg | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  |  | 0.3 | 23.5 | 9 | 0.27 | [5 empty] | 17.5 | 0.4 | 7.4055
[15 empty] | 0.3 | 17.75 | 5.4 | 0.14 | [5 empty] | 17.5 | 0.3 | 5.2912
ERISTYS | sisähalk. | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
PISARANEROTIN | jako | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  |  | Mitoitustilavuusvirralla
TIPPUVESIALLAS | l/s jako | 0.010769 | 0.016923 | 0.022308 | 0.027692 | 0.039231 | 0.020769 | 0.044615 | 0.055385 | 0.010769 | 0.013077 | 0.017692 |  |  | qV | dT | P
PINNOITUS | m² | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 |  |  | 0.125 | 25 | 5.5421 |  |  | 2.7867 | -7.2522 | 0.00070858
MAALAUS | m/s | 0.17706 | 0.27824 | 0.36677 | 0.45531 | 0.64502 | 0.34148 | 0.73355 | 0.91061 | 0.17706 | 0.21501 | 0.29089 |  |  | 0.125 | 22.5 | 4.1866
HOPEAPITOISUUS | Reynolds | 2225.9433 | 3497.9108 | 4610.8825 | 5723.8541 | 8108.7933 | 4292.8906 | 9221.7649 | 11447.7082 | 2225.9433 | 2702.9311 | 3656.9068 |  |  | 0.125 | 17.5 | 2.0577
JÄÄT.SUOJAMUHVEJA | kpl
Tuotekoodit ja huomautukset per positio
1. EC-HEAT-650-450-3-1.6-25K-13-R-9.52
Huom:
2. EC-HEAT-650-450-3-1.6-25K-13-R-9.52
Huom:
3. EC-HEAT-650-450-3-1.6-25K-13-R-9.52
Huom:
4. EC-HEAT-650-450-3-1.6-25K-13-R-9.52
Huom:
Tulevan ilman tiheys | kg/m³ | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.3171 | 1.2698 | 1.2698 | 1.2698
lähtevän ilman tiheys | kg/m³ | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048 | 1.2048
Logaritminen ylilämpötila | K | 21.6404 | 21.6404 | 21.6404 | 21.6404 | 22.2391 | 22.4367 | 23.6045 | 23.6045 | 17.6071 | 17.3803 | 17.6071
Aritmeettinen dT | K | 22.5 | 22.5 | 22.5 | 22.5 | 23.25 | 23.5 | 25 | 25 | 17.75 | 17.5 | 17.75
[14 empty] | 1.6735 | 4.4321 | 84.104
[16 empty] | 1.8875 | 2.6451 | 14.0854

## C5 JÄ-1 (hidden)
TARJOUSNUMEROMME 123729-TK
RIVI |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | [6 empty] | JÄ-1
LUKUMÄÄRÄ | [26 empty] | Tilavuusvirta | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | bar: 1 to 19
KOJE | [26 empty] | Massavirta | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6
KOJENO | [26 empty] | Tuleva ilm | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25
TYYPPI | [26 empty] | Tuleva kosteus-% | 65 | 65 | 65 | 65 | 65 | 45 | 45 | 45 | 65 | 65 | 65 | 50 | 50 | 50
KÄYTTÖ |  |  | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | LTO | LTO | LTO | LTO | LTO |  |  | Magnus-kaava --> |  |  | Tuleva kosteussisältö | 0.012901 | 0.012901 | 0.012901 | 0.012901 | 0.012901 | 0.011953 | 0.011953 | 0.011953 | 0.012901 | 0.012901 | 0.012901 | 0.0098763 | 0.0098763 | 0.0098763
KÄTISYYS | [26 empty] | Lähtevä ilm | 15 | 15.6 | 16.2 | 16.6 | 16.9 | 15.5 | 16.1 | 16.7 | 17 | 17.5 | 17.7 | 16.2 | 16.7 | 17.1
ASENTO |  |  | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | [5 empty] | Lähtevä kosteus-% | 100 | 100 | 99 | 99 | 98 | 99 | 98 | 97 | 99 | 98 | 98 | 86 | 83 | 81
LAMELLIMATERIAALI | [26 empty] | Lähtevä kosteussisältö | 0.01064 | 0.011065 | 0.011389 | 0.011688 | 0.011795 | 0.010881 | 0.011199 | 0.011522 | 0.011995 | 0.01226 | 0.012419 | 0.0098695 | 0.0098327 | 0.0098426 | bar: 1 to 19
KEHYSMATERIAALI | [23 empty] | Magnus-kaava --> |  |  | Latentti teho | 1.3566 | 1.652 | 1.8143 | 1.8187 | 1.9907 | 0.96491 | 0.90577 | 0.64706 | 0.81541 | 0.7684 | 0.72223 | 0.0061233 | 0.052237 | 0.050459 | bar: 1 to 19
LIUOS |  |  | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Etyleenigly | Etyleenigly | Etyleenigly | Etyleenigly | Etyleenigly | [6 empty] | 17.53% | 14.23% | 11.72% | 9.399% | 8.573% | 8.969% | 6.315% | 3.609% | 7.023% | 4.964% | 3.732% | 0.06889% | 0.4408% | 0.3406%
PITOISUUS | % |  | 15: 35; 16: 35; 17: 35; 18: 35; 19: 35 | [5 empty] | Menovesi | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 10 | 10 | 10 | 10 | 10
[27 empty] | Paluuvesi | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 15 | 15 | 15 | 15 | 15 | 15
OP.LEVEYS | mm |  | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | [5 empty] | Keskiarvo | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
OP.KORKEUS | mm |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
KEH.LEVEYS | mm |  | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | [5 empty] | Kokonaisteho | 3.792 | 5.184 | 6 | 7.02 | 7.848 | 6.336 | 7.68 | 8.76 | 3.672 | 4.416 | 5.16 | 3.24 | 4.08 | 4.86
KEH.KORKEUS | mm |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | [5 empty] | Tuntuva teho | 2.412 | 3.4009 | 4.2451 | 5.0652 | 5.8612 | 5.2461 | 6.7054 | 8.0199 | 2.8944 | 3.618 | 4.4019 | 3.1838 | 4.0039 | 4.7637
KEH.SYVYYS | mm |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | [5 empty] | Latentti | 1.38 | 1.7831 | 1.7549 | 1.9548 | 1.9868 | 1.0899 | 0.97464 | 0.7401 | 0.7776 | 0.798 | 0.7581 | 0.05616 | 0.07608 | 0.0963
[27 empty] | Tuntuvan osuus kokonaistehosta | 63.61% | 65.6% | 70.75% | 72.15% | 74.68% | 82.8% | 87.31% | 91.55% | 78.82% | 81.93% | 85.31% | 98.27% | 98.14% | 98.02%
TEHO | kW |  | 3.8 | 5.2 | 6 | 7 | 7.8 | 6.3 | 7.7 | 8.8 | 3.2 | 4.1 | 4.9 | 3.7 | 4.4 | 5.2 | 2.3 | 2.7 | 3 | 3.2 | 3.4
ILMAN TILAVUUSVIRTA | m3/s |  | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | [5 empty] | Tulevan ilman kastepiste | 17.9523 | 17.9523 | 17.9523 | 17.9523 | 17.9523 | 16.7502 | 16.7502 | 16.7502 | 17.9523 | 17.9523 | 17.9523 | 13.8423 | 13.8423 | 13.8423
ILMAN MASSAVIRTA | kg/s |  | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | [5 empty] | Kastepiste vs. vesilämpötilojen lämpötila-alue | 219% | 219% | 219% | 219% | 219% | 195% | 195% | 195% | 159% | 159% | 159% | 76.85% | 76.85% | 76.85%
TULEVA ILMA | oC |  | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
TUL. SUHT. KOSTEUS | % |  | 65 | 65 | 65 | 65 | 65 | 45 | 45 | 45 | 50 | 50 | 50 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | [6 empty] | 63.61% | 65.6% | 70.75% | 72.15% | 74.68% | 82.8% | 87.31% | 91.55% | 78.82% | 81.93% | 85.31% | 98.27% | 98.14% | 98.02%
TULEVA ILM. ENT | kj/kg |  | 58 | 58 | 58 | 58 | 58 | 60.7 | 60.7 | 60.7 | 50.3 | 50.3 | 50.3 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | [6 empty] | 0.18 | 0.25 | 0.29 | 0.34 | 0.37 | 0.3 | 0.37 | 0.42 | 0.18 | 0.21 | 0.25 | 0.15 | 0.19 | 0.23
LÄHTEVÄ ILMA | oC |  | 15 | 15.6 | 16.2 | 16.6 | 16.9 | 15.5 | 16.1 | 16.7 | 16.2 | 16.7 | 17.1 | 17 | 17.5 | 17.7 | 17.4 | 18.4 | 19.1 | 19.8 | 20.4
LÄH. SUHT. KOSTEUS | % |  | 100 | 100 | 99 | 99 | 98 | 99 | 98 | 97 | 86 | 83 | 81 | 99 | 98 | 98 | 98 | 95 | 93 | 89 | 86
LÄHTEVÄ ILM. ENT | kj/kg |  | 42.2 | 43.6 | 45.5 | 46.3 | 47.1 | 43.1 | 44.7 | 46.1 | 41.3 | 41.8 | 42.2 | 47.8 | 48.8 | 49.4 | 48.2 | 50.5 | 51.7 | 52.6 | 53.3 | [6 empty] | 139.3% | 143.7% | 155% | 158.1% | 163.6% | 161.5% | 170.3% | 178.5% | 125.4% | 130.3% | 135.7% | 75.51% | 75.41% | 75.32%
ILMAN NOPEUS | m/s |  | 0.68 | 1.03 | 1.37 | 1.71 | 2.05 | 1.03 | 1.37 | 1.71 | 1.03 | 1.37 | 1.71 | 1.03 | 1.37 | 1.71 | 0.68 | 1.03 | 1.37 | 1.71 | 2.05 | [6 empty] | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Täysin k. | Ositt. k. | Ositt. k. | Ositt. k.
ILMAN PAINEHÄVIÖ | Pa |  | 5 | 10 | 16.4 | 24.1 | 32.9 | 10 | 16.4 | 24.1 | 10 | 16.4 | 24.1 | 10 | 16.4 | 24.1 | 5 | 10 | 16.4 | 24.1 | 32.9
|  |  | 7/12 | [7 empty] | 10/15 | [5 empty] | 7/12 glykoli
TULEVA NESTE | oC |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 7 | 7 | 7
LÄHTEVÄ NESTE | oC |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 12 | 12
NESTEVIRTA | l/s |  | 0.18 | 0.25 | 0.29 | 0.34 | 0.37 | 0.3 | 0.37 | 0.42 | 0.15 | 0.19 | 0.23 | 0.18 | 0.21 | 0.25 | 0.12 | 0.14 | 0.16 | 0.17 | 0.18
NESTE NOPEUS | m/s |  | 0.37 | 0.51 | 0.59 | 0.69 | 0.77 | 0.62 | 0.75 | 0.86 | 0.32 | 0.4 | 0.48 | 0.36 | 0.43 | 0.51 | 0.25 | 0.29 | 0.33 | 0.35 | 0.37
NESTEEN PAINEHÄVIÖ | kPa |  | 3.6 | 6.4 | 8.5 | 11.4 | 14 | 9.4 | 13.5 | 17.4 | 2.6 | 4 | 5.6 | 3.3 | 4.7 | 6.3 | 3.4 | 3.9 | 4.4 | 4.6 | 4.9
PUTKIYHDE | DN |  | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K
HYÖTYSUHDE | %
RIVISYYS |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
LAMELLIJAKO | mm |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
NESTETILAVUUS | l |  | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
PAINO | kg |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
ERISTYS | sisähalk. |  | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
PISARANEROTIN | jako |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
TIPPUVESIALLAS | l/s jako |  | 0.025714 | 0.035714 | 0.041429 | 0.048571 | 0.052857 | 0.042857 | 0.052857 | 0.06 | 0.021429 | 0.027143 | 0.032857 | 0.025714 | 0.03 | 0.035714
PINNOITUS | m² |  | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05
MAALAUS | m/s |  | 0.42278 | 0.5872 | 0.68115 | 0.79859 | 0.86906 | 0.70464 | 0.86906 | 0.9865 | 0.35232 | 0.44627 | 0.54022 | 0.42278 | 0.49325 | 0.5872
HOPEAPITOISUUS | Reynolds |  | 3100.421 | 4306.1402 | 4995.1227 | 5856.3507 | 6373.0875 | 5167.3683 | 6373.0875 | 7234.3156 | 2583.6841 | 3272.6666 | 3961.649 | 3100.421 | 3617.1578 | 4306.1402
JÄÄT.SUOJAMUHVEJA | kpl
Tuotekoodit ja huomautukset per positio
1. EC-COOL-650-450-3-2.5-25K-7-R-9.52 |  |  | 3.792 | 5.184 | 6 | 7.02 | 7.848 | 6.336 | 7.68 | 8.76 | 3.24 | 4.08 | 4.86 | 3.672 | 4.416 | 5.16 | Kokonaisteho
Huom: TUNTUVA TEHO 2.4 kW |  |  | 2.412 | 3.4009 | 4.2451 | 5.0652 | 5.8612 | 5.2461 | 6.7054 | 8.0199 | 3.1838 | 4.0039 | 4.7637 | 2.8944 | 3.618 | 4.4019 | Tuntuva
2. EC-COOL-650-450-3-2.5-25K-7-R-9.52 |  |  | 1.38 | 1.7831 | 1.7549 | 1.9548 | 1.9868 | 1.0899 | 0.97464 | 0.7401 | 0.05616 | 0.07608 | 0.0963 | 0.7776 | 0.798 | 0.7581 | Latentti
Huom: TUNTUVA TEHO 3.4 kW |  |  | 63.61% | 65.6% | 70.75% | 72.15% | 74.68% | 82.8% | 87.31% | 91.55% | 98.27% | 98.14% | 98.02% | 78.82% | 81.93% | 85.31%
3. EC-COOL-650-450-3-2.5-25K-7-R-9.52
Huom: TUNTUVA TEHO 4.2 kW |  |  | 0.18 | 0.25 | 0.29 | 0.34 | 0.37 | 0.3 | 0.37 | 0.42 | 0.15 | 0.19 | 0.23 | 0.18 | 0.21 | 0.25 | virtaama | [24 empty] | 3.7456 | -5.0664 | 0.0063048
4. EC-COOL-650-450-3-2.5-25K-7-R-9.52
Huom: TUNTUVA TEHO 5.0 kW |  |  | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5
|  |  | 3.8 | 5.2 | 6 | 7 | 7.8 | 6.3 | 7.7 | 8.8 | 3.2 | 4.1 | 4.9 | 3.7 | 4.4 | 5.2
Tulevan ilman tiheys | kg/m³ |  | 1.1846 | 0.94649 | 0.94903 | 0.94903 | 0.95159 | 0.94903 | 0.95159 | 0.95416 | 0.98339 | 0.99167 | 0.99727 | 0.94903 | 0.95159 | 0.95159
lähtevän ilman tiheys | kg/m³ |  | 1.2257 | 1.115 | 1.1084 | 1.1056 | 1.1028 | 1.1168 | 1.1112 | 1.1063 | 1.1232 | 1.1214 | 1.12 | 1.1004 | 1.097 | 1.095
dT1 = Tilma,in-Tneste,out | K |  | 13 | 13 | 13 | 13 | 13 | 18 | 18 | 18 | 10 | 10 | 10 | 10 | 10 | 10
dT2 = Tilma,out-Tneste,in | K |  | 8 | 8.6 | 9.2 | 9.6 | 9.9 | 8.5 | 9.1 | 9.7 | 6.2 | 6.7 | 7.1 | 7 | 7.5 | 7.7
Logaritminen alilämpötila LMTD | K |  | 10.2985 | 10.6489 | 10.9907 | 11.2142 | 11.3797 | 12.6615 | 13.048 | 13.4251 | 7.9492 | 8.2402 | 8.4674 | 8.411 | 8.6901 | 8.8
Aritmeettinen dT | K |  | 10.5 | 10.8 | 11.1 | 11.3 | 11.45 | 13.25 | 13.55 | 13.85 | 8.1 | 8.35 | 8.55 | 8.5 | 8.75 | 8.85
Veden keskilämpötila |  |  | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
Kastepiste |  |  | 17.9523 | 17.9523 | 17.9523 | 17.9523 | 17.9523 | 16.7502 | 16.7502 | 16.7502 | 13.8423 | 13.8423 | 13.8423 | 17.9523 | 17.9523 | 17.9523
|  |  | Täysin kondensoiva | [7 empty] | 77 % kondensoiva |  |  | Täysin kondensoiva
[29 empty] | 1.718 | 4.3719 | 79.1979 |  |  |  |  | 1.8729 | 4.471 | 87.4475
|  | y | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 1.1369 | 1.1369 | 1.1369 | 0.95036 | 0.95036 | 0.95036 | 1.2127 | 1.2127 | 1.2127
|  |  | 288.2652 | 288.2652 | 288.2652 | 288.2652 | 288.2652 | 270.2335 | 270.2335 | 270.2335 | 225.9012 | 225.9012 | 225.9012 | 288.2652 | 288.2652 | 288.2652
|  |  | 16.0573 | 16.0573 | 16.0573 | 16.0573 | 16.0573 | 16.1331 | 16.1331 | 16.1331 | 16.3196 | 16.3196 | 16.3196 | 16.0573 | 16.0573 | 16.0573
|  |  | 0.2: Täysin kondensoiva 500 l/s | [8 empty] | 0.3903
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.6: qW |  |  |  |  | Mitoituspiste
|  |  | 0.5 | 13.85 | 13.4251 | 8.8 | 0.42 |  | 1.176 | -0.91253 | 0.40151
|  |  | 0.2: 0.5; 0.3: 11.3; 0.4: 11.2142; 0.5: 7; 0.6: 0.34 |  |  |  |  | Tilavuusvirta |  | 125 | l/s | Kosteus | Tiheys |  | cp |  | Aputermi |  | Kosteussisältö | [5 empty] | Ilmapuolen painehäviö
|  |  | 0.2: 0.5; 0.3: 8.85; 0.4: 8.8; 0.5: 5.2; 0.6: 0.25 |  |  |  |  | TLTO |  | 25 | °C | 65 | 1.1846 | kg/m³ | 1010 | J/kgK | 1.2127 | Saapuva | 0.012901 | kg/kg |  |  |  |  | 2.2245 | Pa
| Osittain kond |  | 0.2: 0.5; 0.3: 8.55; 0.4: 8.4674; 0.5: 4.9; 0.6: 0.48 |  |  |  |  | TTULO |  | 17 | °C | 93.9108 | 1.2172 | kg/m³ | 1008.4 | J/kgK |  | Lähtevä | 0.011367 | kg/kg | Täysin kondensoiva tilanne
[25 empty] | 98.6 | [6 empty] | 0.011367 | kg/kg | Osittain kondensoiva tilanne
|  |  | 0.2: Täysin kondensoiva 400 l/s |  |  |  |  | Tavoitelämpötilat lämmitysvedelle | [10 empty] | 0.93911
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.6: qW |  |  |  |  | TMENOVESI |  | 7 | °C | [7 empty] | 0.93911
|  |  | 0.2: 0.4; 0.3: 13.55; 0.4: 13.048; 0.5: 7.7; 0.6: 0.37; 0.4: 1.2804; 0.5: -1.2939; 0.3: 0.27421 |  |  |  |  | TPALUUVESI |  | 12 | °C |  | dT | 11.5
|  |  | 0.2: 0.4; 0.3: 11.1; 0.4: 10.9907; 0.5: 6; 0.6: 0.29 |  |  |  |  | dT1 |  | 13 |  |  | LMTD | 11.4345
|  |  | 0.2: 0.4; 0.3: 8.75; 0.4: 8.6901; 0.5: 4.4; 0.6: 0.21 |  |  |  |  | dT2 |  | 10 |  |  |  |  | Maksimi | 250% | Tarkistus | KA
| Osittain kond |  | 0.2: 0.4; 0.3: 8.35; 0.4: 8.2402; 0.5: 4.1; 0.6: 0.4 |  |  |  |  | Kastepiste | TLTO | 17.9523 | °C |  | Osuus vesilämpötila-alueesta |  |  | 219% | 219% |  | 11.89% | Kosteussisällön lasku
|  |  | 0.2: Täysin kondensoiva 300 l/s |  |  |  |  | Tuntuvan tehon tarve |  | 1.212 | kW |  | Latentti | 0.57564 | kW | <-- massavirta ja veden höyrystymislämpö
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.6: qW |  |  |  |  | Kokonaistehon tarve |  | 1.7876 | kW |  | Latentti | 0.57564 | kW
|  |  | 0.2: 0.3; 0.3: 13.25; 0.4: 12.6615; 0.5: 6.3; 0.6: 0.3; 0.4: 1.2052; 0.5: -1.2545; 0.3: 0.28522 |  |  |  |  | Tarvittava dT |  | 6.9287 | K |  | Valinta | 0.57564 | kW
|  |  | 0.3 | 10.8 | 10.6489 | 5.2 | 0.25
|  |  | 0.3 | 8.5 | 8.411 | 3.7 | 0.18
| Osittain kond |  | 0.2: 0.3; 0.3: 8.1; 0.4: 7.9492; 0.5: 3.2; 0.6: 0.32 |  |  |  |  | Mitoitus menoveden lämpötilan mukaan |  |  |  |  | Mitoitus paluuveden lämpötilan mukaan | [5 empty] | Mitoitus tavoitevesien mukaan
[21 empty] | TMENOVESI |  | 7 | °C |  | TMENOVESI |  | 16.1426 | °C |  |  | TMENOVESI |  | 7 | °C
[21 empty] | TPALUUVESI |  | 21.1426 | °C |  | TPALUUVESI |  | 12 | °C |  |  | TPALUUVESI |  | 12 | °C
|  |  | 0.2: Mitoitusilmavirralla, täysin kondensoiva; 0.5: dT; 0.3: qV; 0.4: P |  |  |  |  | Virtaama |  | 0.030195 | l/s |  | Virtaama |  | -0.10309 | l/s |  |  | Virtaama |  | 0.085409 | l/s
|  |  | 0.5: 13; 0.3: 0.5; 0.4: 8.1986 |  |  |  |  | Painehäviö |  | 0.1244 | kPa |  | Painehäviö |  | #NUM! | kPa |  |  | Painehäviö |  | 0.87206 | kPa
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.5: 13; 0.3: 0.4; 0.4: 7.3173 | [5 empty] | dT | 6.9287 |  |  |  | dT | 6.9287
|  |  | 0.125 |  | 13 | 3.9713 |  |  | 1.2685 | -1.8745 | 0.15344 |  | 13 | 0.3 | 6.2758 | [7 empty] | 3.8574
|  |  | 0.2: 0.125; 0.4: 10.5; 0.5: 3.0288; 0.5: 0.5237; 0.3: 2.4681; 0.4: 11.7999 | [6 empty] | 10
|  |  | 0.2: 0.125; 0.4: 7; 0.5: 1.811 | [6 empty] | 6.4483
[13 empty] | dT | qV | P
|  |  | 0.5: 10.5; 0.3: 0.5; 0.4: 6.3776 |  |  |  |  | Jakotukista |  | 7 | kpl |  | Jakotukista |  | 7 | kpl |  |  | Jakotukista |  | 7 | kpl
|  |  | 0.5: 10.5; 0.3: 0.4; 0.4: 5.5666 |  |  |  |  | Virtaama |  | 0.0043136 | m/s |  | Virtaama |  | -0.014727 | m/s |  |  | Virtaama |  | 0.012201 | m/s
|  |  | 0.5: 10.5; 0.3: 0.3; 0.4: 4.8516 |  |  |  |  | Putken sisähalkaisija |  | 8.8 | mm |  | Putken sisähalkaisija |  | 8.8 | mm |  |  | Putken sisähalkaisija |  | 8.8 | mm
|  |  | 0.5: 0.53267; 0.3: 2.2158; 0.4: 9.169 |  |  |  |  | Virtausnopeus |  | 0.070923 | m/s |  | Virtausnopeus |  | -0.24213 | m/s |  |  | Virtausnopeus |  | 0.20061 | m/s
[21 empty] | Reynolds-luku |  | 520.104 |  |  | Reynolds-luku |  | -1775.6056 |  |  |  | Reynolds-luku |  | 1471.1246
[13 empty] | dT | qV | P
[13 empty] | 7 | 0.5 | 3.9588
[13 empty] | 7 | 0.4 | 3.3123
[13 empty] | 7 | 0.3 | 2.9762
[13 empty] | 0.54969 | 1.7369 | 5.6798

## C5 JÄ-2 (hidden)
TARJOUSNUMEROMME 123732-TK
RIVI |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | [6 empty] | JÄ-2
LUKUMÄÄRÄ | [26 empty] | Tilavuusvirta | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | bar: 1 to 19
KOJE | [26 empty] | Massavirta | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6
KOJENO | [26 empty] | Tuleva ilm | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 25
TYYPPI | [26 empty] | Tuleva kosteus-% | 65 | 65 | 65 | 65 | 50 | 50 | 50 | 50 | 45 | 45 | 45 | 65 | 65 | 65
KÄYTTÖ |  |  | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | JÄÄ.V | LTO | LTO | LTO | LTO | LTO | [5 empty] | Tuleva kosteussisältö | 0.012901 | 0.012901 | 0.012901 | 0.012901 | 0.0098763 | 0.0098763 | 0.0098763 | 0.0098763 | 0.011953 | 0.011953 | 0.011953 | 0.012901 | 0.012901 | 0.012901
KÄTISYYS | [26 empty] | Lähtevä ilm | 18 | 18.9 | 17.1 | 17.4 | 17.1 | 15.8 | 16.3 | 16.7 | 16.1 | 16.7 | 17.3 | 15.5 | 16 | 16.5
ASENTO |  |  | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | Pysty | [5 empty] | Lähtevä kosteus-% | 97 | 94 | 99 | 99 | 81 | 88 | 85 | 83 | 99 | 98 | 96 | 100 | 100 | 100
LAMELLIMATERIAALI | [26 empty] | Lähtevä kosteussisältö | 0.012529 | 0.012853 | 0.012072 | 0.012308 | 0.0098426 | 0.0098437 | 0.0098163 | 0.0098327 | 0.011315 | 0.011643 | 0.011852 | 0.010993 | 0.011357 | 0.011732 | bar: 1 to 19
KEHYSMATERIAALI | [26 empty] | Latentti teho | 0.22292 | 0.04281 | 0.99392 | 0.88846 | 0.06055 | 0.029266 | 0.071982 | 0.065296 | 0.57461 | 0.37244 | 0.15274 | 1.7168 | 1.8521 | 1.7527 | bar: 1 to 19
LIUOS |  |  | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Vesi | Etyleenigly | Etyleenigly | Etyleenigly | Etyleenigly | Etyleenigly | [6 empty] | 2.88% | 0.3687% | 6.42% | 4.591% | 0.3406% | 0.3293% | 0.6074% | 0.4408% | 5.341% | 2.596% | 0.8519% | 14.79% | 11.96% | 9.058%
PITOISUUS | % |  | 15: 35; 16: 35; 17: 35; 18: 35; 19: 35 | [5 empty] | Menovesi | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[27 empty] | Paluuvesi | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15
OP.LEVEYS | mm |  | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | [5 empty] | Keskiarvo | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12.5 | 12.5 | 12.5
OP.KORKEUS | mm |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
KEH.LEVEYS | mm |  | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | [5 empty] | Kokonaisteho | 1.872 | 2.304 | 4.8 | 5.58 | 5.832 | 3.384 | 4.272 | 5.1 | 5.688 | 6.912 | 7.98 | 5.22 | 6.336 | 7.08
KEH.KORKEUS | mm |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | [5 empty] | Tuntuva teho | 1.6884 | 2.207 | 3.811 | 4.5828 | 5.7164 | 3.3286 | 4.1969 | 5.0049 | 5.029 | 6.4159 | 7.6581 | 3.4371 | 4.3416 | 5.1255
KEH.SYVYYS | mm |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | [5 empty] | Latentti | 0.1836 | 0.09702 | 0.98904 | 0.9972 | 0.11556 | 0.05544 | 0.07512 | 0.0951 | 0.65898 | 0.49608 | 0.3219 | 1.7829 | 1.9944 | 1.9545
[27 empty] | Tuntuvan osuus kokonaistehosta | 90.19% | 95.79% | 79.39% | 82.13% | 98.02% | 98.36% | 98.24% | 98.14% | 88.41% | 92.82% | 95.97% | 65.84% | 68.52% | 72.39%
TEHO | kW |  | 1.9 | 2.3 | 4.8 | 5.6 | 5.8 | 3.4 | 4.3 | 5.1 | 5.7 | 6.9 | 8 | 5.2 | 6.3 | 7.1 | 1.7 | 1.9 | 2.1 | 2.2 | 2.3
ILMAN TILAVUUSVIRTA | m3/s |  | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | [5 empty] | Tulevan ilman kastepiste | 17.9523 | 17.9523 | 17.9523 | 17.9523 | 13.8423 | 13.8423 | 13.8423 | 13.8423 | 16.7502 | 16.7502 | 16.7502 | 17.9523 | 17.9523 | 17.9523
ILMAN MASSAVIRTA | kg/s |  | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 | 0.36 | 0.48 | 0.6 | 0.24 | 0.36 | 0.48 | 0.6 | 0.72 | [5 empty] | Kastepiste vs. vesilämpötilojen lämpötila-alue | 99.4% | 99.4% | 99.4% | 99.4% | 48.03% | 48.03% | 48.03% | 48.03% | 84.38% | 84.38% | 84.38% | 159% | 159% | 159%
TULEVA ILMA | oC |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
TUL. SUHT. KOSTEUS | % |  | 65 | 65 | 65 | 65 | 50 | 50 | 50 | 50 | 45 | 45 | 45 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | [6 empty] | 90.19% | 95.79% | 79.39% | 82.13% | 98.02% | 98.36% | 98.24% | 98.14% | 88.41% | 92.82% | 95.97% | 65.84% | 68.52% | 72.39%
TULEVA ILM. ENT | kj/kg |  | 58 | 58 | 58 | 58 | 50.3 | 50.3 | 50.3 | 50.3 | 60.7 | 60.7 | 60.7 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | [6 empty] | 0.06 | 0.07 | 0.14 | 0.17 | 0.17 | 0.1 | 0.13 | 0.15 | 0.17 | 0.21 | 0.24 | 0.25 | 0.3 | 0.34
LÄHTEVÄ ILMA | oC |  | 18 | 18.9 | 17.1 | 17.4 | 17.1 | 15.8 | 16.3 | 16.7 | 16.1 | 16.7 | 17.3 | 15.5 | 16 | 16.5 | 18.6 | 19.9 | 20.7 | 21.4 | 21.8
LÄH. SUHT. KOSTEUS | % |  | 97 | 94 | 99 | 99 | 81 | 88 | 85 | 83 | 99 | 98 | 96 | 100 | 100 | 100 | 95 | 89 | 85 | 81 | 78
LÄHTEVÄ ILM. ENT | kj/kg |  | 50.2 | 51.6 | 48 | 48.7 | 42.2 | 40.9 | 41.4 | 41.8 | 44.9 | 46.3 | 47.4 | 43.5 | 44.8 | 46.2 | 51.1 | 52.7 | 53.5 | 54.3 | 54.8 | [6 empty] | 89.65% | 95.22% | 78.92% | 81.64% | 47.08% | 47.24% | 47.18% | 47.13% | 74.6% | 78.32% | 80.97% | 104.7% | 109% | 115.1%
ILMAN NOPEUS | m/s |  | 0.68 | 1.03 | 1.37 | 1.71 | 2.05 | 1.03 | 1.37 | 1.71 | 1.03 | 1.37 | 1.71 | 1.03 | 1.37 | 1.71 | 0.68 | 1.03 | 1.37 | 1.71 | 2.05
ILMAN PAINEHÄVIÖ | Pa |  | 6.7 | 13.4 | 21.9 | 32.1 | 43.8 | 13.4 | 21.9 | 32.1 | 13.4 | 21.9 | 32.1 | 13.4 | 21.9 | 32.1 | 6.7 | 13.4 | 21.9 | 32.1 | 43.8
|  |  | 10/18 | [10 empty] | 10/15 |  |  | 10/18 glykoli
TULEVA NESTE | oC |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [14 empty] | 2.7191 | -3.5032 | 0.030102
LÄHTEVÄ NESTE | oC |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18
NESTEVIRTA | l/s |  | 0.06 | 0.07 | 0.14 | 0.17 | 0.17 | 0.1 | 0.13 | 0.15 | 0.17 | 0.21 | 0.24 | 0.25 | 0.3 | 0.34 | 0.05 | 0.06 | 0.07 | 0.07 | 0.08
NESTE NOPEUS | m/s |  | 0.16 | 0.2 | 0.41 | 0.48 | 0.5 | 0.29 | 0.37 | 0.44 | 0.49 | 0.6 | 0.68 | 0.72 | 0.87 | 0.97 | 0.16 | 0.18 | 0.2 | 0.21 | 0.22
NESTEEN PAINEHÄVIÖ | kPa |  | 1.3 | 1.6 | 8.2 | 10.9 | 12 | 4.3 | 6.6 | 9.3 | 11.5 | 16.6 | 21.6 | 23.8 | 34.3 | 42.6 | 2.9 | 3.3 | 3.7 | 3.9 | 4
PUTKIYHDE | DN |  | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K | 25 K
HYÖTYSUHDE | %
| Reynolds |  | 0 | 4166.6667 | 8541.6667 | 10000 | 10416.6667 | 6041.6667 | 7708.3333 | 9166.6667 | 10208.3333 | 12500 | 14166.6667 | 15000 | 18125 | 20208.3333
RIVISYYS |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
LAMELLIJAKO | mm |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
NESTETILAVUUS | l |  | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
PAINO | kg |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
ERISTYS | sisähalk. |  | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
PISARANEROTIN | jako |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
TIPPUVESIALLAS | l/s jako |  | 0.012 | 0.014 | 0.028 | 0.034 | 0.034 | 0.02 | 0.026 | 0.03 | 0.034 | 0.042 | 0.048 | 0.05 | 0.06 | 0.068 | 0.01 | 0.012 | 0.014 | 0.014 | 0.016
PINNOITUS | m² |  | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05 | 6.0821e-05
MAALAUS | m/s |  | 0.1973 | 0.23018 | 0.46037 | 0.55902 | 0.55902 | 0.32883 | 0.42748 | 0.49325 | 0.55902 | 0.69055 | 0.7892 | 0.82208 | 0.9865 | 1.118 | 0.16442 | 0.1973 | 0.23018 | 0.23018 | 0.26307
HOPEAPITOISUUS | Reynolds |  | 1446.8631 | 1688.007 | 3376.0139 | 4099.4455 | 4099.4455 | 2411.4385 | 3134.8701 | 3617.1578 | 4099.4455 | 5064.0209 | 5787.4525 | 6028.5963 | 7234.3156 | 8198.891
JÄÄT.SUOJAMUHVEJA | kpl
Tuotekoodit ja huomautukset per positio
1. EC-COOL-650-450-4-2.5-25K-5-R-9.52 |  |  | 1.872 | 2.304 | 4.8 | 5.58 | 5.832 | 3.384 | 4.272 | 5.1 | 5.688 | 6.912 | 7.98 | 5.22 | 6.336 | 7.08 | Kokonaisteho
Huom: TUNTUVA TEHO 1.7 kW |  |  | 1.6884 | 2.207 | 3.811 | 4.5828 | 5.7164 | 3.3286 | 4.1969 | 5.0049 | 5.029 | 6.4159 | 7.6581 | 3.4371 | 4.3416 | 5.1255 | Tuntuva
2. EC-COOL-650-450-4-2.5-25K-5-R-9.52 |  |  | 0.1836 | 0.09702 | 0.98904 | 0.9972 | 0.11556 | 0.05544 | 0.07512 | 0.0951 | 0.65898 | 0.49608 | 0.3219 | 1.7829 | 1.9944 | 1.9545 | Latentti
Huom: TUNTUVA TEHO 2.2 kW |  |  | 90.19% | 95.79% | 79.39% | 82.13% | 98.02% | 98.36% | 98.24% | 98.14% | 88.41% | 92.82% | 95.97% | 65.84% | 68.52% | 72.39%
3. EC-COOL-650-450-4-2.5-25K-5-R-9.52
Huom: TUNTUVA TEHO 3.8 kW |  |  | 0.06 | 0.07 | 0.14 | 0.17 | 0.17 | 0.1 | 0.13 | 0.15 | 0.17 | 0.21 | 0.24 | 0.25 | 0.3 | 0.34 | virtaama
4. EC-COOL-650-450-4-2.5-25K-5-R-9.52
Huom: TUNTUVA TEHO 4.6 kW |  |  | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5
|  |  | 1.9 | 2.3 | 4.8 | 5.6 | 5.8 | 3.4 | 4.3 | 5.1 | 5.7 | 6.9 | 8 | 5.2 | 6.3 | 7.1
Tulevan ilman tiheys | kg/m³ |  | 1.1846 | 1.1846 | 1.1846 | 1.1846 | 1.1846 | 1.1846 | 1.1846 | 1.1846 | 1.165 | 1.165 | 1.165 | 1.1846 | 1.1846 | 1.1846
lähtevän ilman tiheys | kg/m³ |  | 1.2131 | 1.2093 | 1.2168 | 1.2156 | 1.2168 | 1.2223 | 1.2202 | 1.2185 | 1.221 | 1.2185 | 1.216 | 1.2236 | 1.2215 | 1.2193
dT1 = Tilma,in-Tneste,out | K |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 12 | 12 | 12 | 10 | 10 | 10
dT2 = Tilma,out-Tneste,in | K |  | 8 | 8.9 | 7.1 | 7.4 | 7.1 | 5.8 | 6.3 | 6.7 | 6.1 | 6.7 | 7.3 | 5.5 | 6 | 6.5
Logaritminen alilämpötila LMTD | K |  | 7.4889 | 7.912 | 7.0499 | 7.1981 | 7.0499 | 6.3812 | 6.6439 | 6.8489 | 8.7198 | 9.094 | 9.4561 | 7.5271 | 7.8305 | 8.1247
Aritmeettinen dT | K |  | 7.5 | 7.95 | 7.05 | 7.2 | 7.05 | 6.4 | 6.65 | 6.85 | 9.05 | 9.35 | 9.65 | 7.75 | 8 | 8.25
Veden keskilämpötila |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12.5 | 12.5 | 12.5
Kastepiste |  |  | 17.9523 | 17.9523 | 17.9523 | 17.9523 | 13.8423 | 13.8423 | 13.8423 | 13.8423 | 16.7502 | 16.7502 | 16.7502 | 17.9523 | 17.9523 | 17.9523
[29 empty] | 1.7095 | 4.6534 | 104.938 |  |  |  |  | 2.0217 | 5.9948 | 401.3394
|  | y | 1.2127 | 1.2127 | 1.2127 | 1.2127 | 0.95036 | 0.95036 | 0.95036 | 0.95036 | 1.1369 | 1.1369 | 1.1369 | 1.2127 | 1.2127 | 1.2127
|  |  | 288.2652 | 288.2652 | 288.2652 | 288.2652 | 225.9012 | 225.9012 | 225.9012 | 225.9012 | 270.2335 | 270.2335 | 270.2335 | 288.2652 | 288.2652 | 288.2652
|  |  | 16.0573 | 16.0573 | 16.0573 | 16.0573 | 16.3196 | 16.3196 | 16.3196 | 16.3196 | 16.1331 | 16.1331 | 16.1331 | 16.0573 | 16.0573 | 16.0573
Täysin kondensoiva 500 l/s
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.6: qW |  |  |  |  | Mitoituspiste
|  |  | 0.5 | 6.85 | 6.8489 | 5.1 | 0.15 |  | 1.7716 | -1.7775 | 0.16906
|  |  | 0.2: 0.5; 0.3: 7.2; 0.4: 7.1981; 0.5: 5.6; 0.6: 0.17 |  |  |  |  | Tilavuusvirta |  | 125 | l/s | Kosteus | Tiheys |  | cp |  | Aputermi |  | Kosteussisältö | [5 empty] | Ilmapuolen painehäviö
|  |  | 0.2: 0.5; 0.3: 8.25; 0.4: 8.1247; 0.5: 7.1; 0.6: 0.34 |  |  |  |  | TLTO |  | 25 | °C | 65 | 1.1846 | kg/m³ | 1010 | J/kgK | 1.2127 |  | 0.012901 | kg/kg |  |  |  |  | 2.9997 | Pa
| Osittain kond |  | 0.2: 0.5; 0.3: 9.65; 0.4: 9.4561; 0.5: 8; 0.6: 0.68 |  |  |  |  | TTULO |  | 17 | °C | 85.5963 | 1.2172 | kg/m³ | 1008.4 | J/kgK |  |  | 0.010344 | kg/kg | Täysin kondensoiva tilanne
[25 empty] | 98.6 | [6 empty] | 0.010344 | kg/kg | Osittain kondensoiva tilanne
|  |  | 0.2: Täysin kondensoiva 400 l/s |  |  |  |  | Tavoitelämpötilat lämmitysvedelle | [10 empty] | 0.85596 | [9 empty] | s
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.6: qW |  |  |  |  | TMENOVESI |  | 7 | °C | [7 empty] | 0.85596
|  |  | 0.2: 0.4; 0.3: 6.65; 0.4: 6.6439; 0.5: 4.3; 0.6: 0.13; 0.4: 2.0801; 0.5: -2.487; 0.3: 0.083161 |  |  |  |  | TPALUUVESI |  | 12 | °C |  | dT | 11.5
|  |  | 0.2: 0.4; 0.3: 7.05; 0.4: 7.0499; 0.5: 4.8; 0.6: 0.14 |  |  |  |  | dT1 |  | 13 |  |  | LMTD | 11.4345
|  |  | 0.2: 0.4; 0.3: 8; 0.4: 7.8305; 0.5: 6.3; 0.6: 0.3 |  |  |  |  | dT2 |  | 10 |  |  |  |  | Maksimi | 200%
| Osittain kond |  | 0.2: 0.4; 0.3: 9.35; 0.4: 9.094; 0.5: 6.9; 0.6: 0.6 |  |  |  |  | Kastepiste | TLTO | 17.9523 | °C |  | Osuus vesilämpötila-alueesta |  |  | 219% | 200% |  | 19.82% | Kosteussisällön lasku
|  |  | 0.2: Täysin kondensoiva 300 l/s |  |  |  |  | Tuntuvan tehon tarve |  | 1.212 | kW |  | Latentti | 0.95959 | kW
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.6: qW |  |  |  |  | Kokonaistehon tarve |  | 2.1716 | kW |  | Latentti | 0.95959 | kW
|  |  | 0.2: 0.3; 0.3: 6.4; 0.4: 6.3812; 0.5: 3.4; 0.6: 0.1; 0.4: 2.2199; 0.5: -2.8971; 0.3: 0.055184 |  |  |  |  | Tarvittava dT |  | 6.4981 | K |  | Valinta | 0.95959 | kW
|  |  | 0.3 | 7.75 | 7.5271 | 5.2 | 0.25
|  |  | 0.3 | 7.75 | 7.5271 | 5.2 | 0.25
| Osittain kond |  | 0.2: 0.3; 0.3: 9.05; 0.4: 8.7198; 0.5: 5.7; 0.6: 0.49 |  |  |  |  | Mitoitus menoveden lämpötilan mukaan |  |  |  |  | Mitoitus paluuveden lämpötilan mukaan | [5 empty] | Mitoitus tavoitevesien mukaan
[21 empty] | TMENOVESI |  | 7 | °C |  | TMENOVESI |  | 17.0038 | °C |  |  | TMENOVESI |  | 7 | °C
[21 empty] | TPALUUVESI |  | 22.0038 | °C |  | TPALUUVESI |  | 12 | °C |  |  | TPALUUVESI |  | 12 | °C
|  |  | 0.2: Mitoitusilmavirralla, täysin kondensoiva; 0.5: dT; 0.3: qV; 0.4: P |  |  |  |  | Virtaama |  | 0.034576 | l/s |  | Virtaama |  | -0.10367 | l/s |  |  | Virtaama |  | 0.10375 | l/s
|  |  | 0.5: 14; 0.3: 0.5; 0.4: 18.134 |  |  |  |  | Painehäviö |  | 0.44596 | kPa |  | Painehäviö |  | #NUM! | kPa |  |  | Painehäviö |  | 4.1127 | kPa
|  |  | 0.2: qV; 0.3: dT; 0.4: LMTD; 0.5: P; 0.5: 14; 0.3: 0.4; 0.4: 20.1343 | [5 empty] | dT | 6.4981 |  |  |  | dT | 6.4981
|  |  | 0.125 | 14 |  | 21.7969 |  |  | 3.0048 | -4.8481 | 0.0078435 |  | 14 | 0.3 | 19.3259 | [7 empty] | 2.9962
|  |  | 0.2: 0.125; 0.3: 11; 0.5: 10.5605; 0.5: -0.11201; 0.3: 2.8488; 0.4: 17.2678 | [6 empty] | 10
|  |  | 0.2: 0.125; 0.3: 7; 0.5: 2.7156 | [6 empty] | 5.8111
[13 empty] | dT | qV | P
|  |  | 0.5: 11; 0.3: 0.5; 0.4: 11.829 |  |  |  |  | Jakotukista |  | 5 | kpl |  | Jakotukista |  | 5 | kpl |  |  | Jakotukista |  | 5 | kpl
|  |  | 0.5: 11; 0.3: 0.4; 0.4: 12.1922 |  |  |  |  | Virtaama |  | 0.0069151 | m/s |  | Virtaama |  | -0.020735 | m/s |  |  | Virtaama |  | 0.020751 | m/s
|  |  | 0.5: 11; 0.3: 0.3; 0.4: 11.3145 |  |  |  |  | Putken sisähalkaisija |  | 8.8 | mm |  | Putken sisähalkaisija |  | 8.8 | mm |  |  | Putken sisähalkaisija |  | 8.8 | mm
|  |  | 0.5: 0.095204; 0.3: 2.5551; 0.4: 12.8725 |  |  |  |  | Virtausnopeus |  | 0.1137 | m/s |  | Virtausnopeus |  | -0.34092 | m/s |  |  | Virtausnopeus |  | 0.34117 | m/s
[21 empty] | Reynolds-luku |  | 833.7713 |  |  | Reynolds-luku |  | -2500.0524 |  |  |  | Reynolds-luku |  | 2501.9453
[13 empty] | dT | qV | P
[13 empty] | 7 | 0.5 | 5.3113
[13 empty] | 7 | 0.4 | 4.7619
[13 empty] | 7 | 0.3 | 4.1483
[13 empty] | 0.48357 | 2.0046 | 7.4228

## Muutoslogi (hidden)
Pvm | Versio | Muutokset | Tekijä | Lähetetty asiakkaalle | Asiakkaalle lähetetyn tiedoston nimi
2018-12-20 | 1.0 | Ohjelma luotu | JK | 2018-12-20 | Model 60 laskentaohjelma, ver. 1.0.xlsx
2019-01-11 | 2.0 | Lisätty Model 100 tulokset, tarkennettu Model 60 ilmamääriä | JK | 2019-01-11 | Airfi laskentaohjelma_v2.0.xlsx
2019-02-01 | 3.0 | Lisätty Model 150 tulokset | JK | 2019-02-01 | Airfi laskentaohjelma_v3.0.xlsx
2019-02-18 | 3.1 | SEC-laskenta, päivitetty elektroniikan teho, hyötysuhteet ja tulostuksen muotoiluja, vastuullisuustekstit | JK | 2019-02-18 | Airfi laskentaohjelma_v3.1.xlsx
2019-02-25 | 4.0 | Yhdistetty vuosihyötysuhteen laskenta, päivitetty minimijäteilman arvo ja mallien kennohyötysuhteet | JK | 2019-02-25 | Airfi laskentaohjelma_4.0.xlsx
2019-03-18 | 4.1 | Korjattu käyttöalue minimi-ilmavirrat 20 l/s (model 60/100) ja 40 l/s (Model 150) | JK | 2019-03-18 | Airfi laskentaohjelma_4.1.xlsx
2019-06-14 | 4.2 | Muutettu käyttöalue minimi-ilmavirrat 18 l/s (Model 60/100) | JK | 2019-06-14 | Airfi laskentaohjelma_4.2.xlsx
2019-06-18 | 4.3 | Muutettu käyttöalue minimi-ilmavirrat 30 l/s (Model 150) | JK | 2019-06-18 | Airfi laskentaohjelma_4.3.xlsx
2019-11-18 | 4.4 | Poistettu Model 150 dB-paketti, poistettu jälkilämmityspaterin tehontarpeen tulostus | JK | 2019-11-19 | Airfi laskentaohjelma_4.4.xlsx
2019-12-03 | 4.5 | Lisätty keittiöohituksen tulokset Model 60 ja 100 | JK | 2019-12-04 | Airfi laskentaohjelma_4.5.xlsx
2021-01-27 | 4.6 | Lisätty ohjelman tekijäksi Zenner + Zenner logo | JK | 2021-02-18 | Airfi laskentaohjelma_4.6.xlsx
2021-05-14 | 5.0 | Lisätään uusi kone + patterimitoitus, lähetetään kommentoitavaksi | JK | 2021-05-14 | Airfi laskentaohjelma_5.0.xlsx
2021-05-28 | 5.1 | Jaettu Model 300 -> Model 250 ja 350. Lisäksi pieniä korjauksia kommenttien perusteella. | JU+JK | 2021-05-28 | Airfi laskentaohjelma_5.1.xlsx
2021-06-11 | 5.2 | Korjattu virheellinen tulostus dB-paketin kanssa | JK | 2021-06-11 | Airfi laskentaohjelma_5.2.xlsx
2021-07-19 | 5.3 | Lisätty Model 130 | JK | 20.7.2021 / HK | Airfi laskentaohjelma_5.3.xlsx
2021-07-25 | 5.4 | Muutettu koneiden järjestys suuruusjärjestykseen, lisätty Model 130 keittiöohitus + pieni korjaus ohj.jännitelaskentaan 9V-10V | JK | 2021-07-25 | Airfi laskentaohjelma_5.4.xlsx
2023-03-06 | 5.5 | Lisätty kielivalinta ENG, SWE, GER | JK/HR | 2023-03-06 | Airfi laskentaohjelma_5.5.xlsx
2023-03-09 | 5.6 | Suomen säädataksi muutettu TRY2020 (vanhat datat poistettu). Lisätty ulkomaiden säädata Riuska:sta. Lisätty toiminnallisuudet maan ja kaupunkien valitsemiselle. | PR | 2023-03-13 | Airfi laskentaohjelma_5.6.xlsx
2023-11-02 | 5.7 | Lisätty tehostustilan laskenta (samalla muutettu tulostuksen sijoitteluja), otettu pois käytöstä muiden maiden säävalinta, Suomen säädata TRY2020 | JK | 2023-11-03 | Airfi laskentaohjelma_5.7.xlsx
2023-11-10 | 5.8 | Lisätty tilaajan 3.11.2023 antamat muutostoiveet (Kielivalinnan vaikutus HS-laskentaan, tilavuusvirran syötön yksiköihin ja tulostuksen teksteihin + pieniä muita korjauksia) | JK | 2023-11-10 | Airfi laskentaohjelma_5.8.xlsx
2024-02-13 | 5.9 | Lisätty Bukarest säädatat ja ohjeteksti, että sähkötehon arvot sisältävät myös koneen elektroniikan. | JK | 2024-02-13 | Airfi laskentaohjelma_5.9.xlsx
2024-03-14 | 6.0 | Muutoksia vuosihyötysuhdelaskentaan ja tulostukseen (mm. kennon hyötysuhteet, tilavusvirtariippuvaiset hyötysuhteet, tuloilma rajoituksen valinta yms.) | JK | 2024-03-14 | Airfi laskentaohjelma_6.0.xlsx
2024-09-10 | 6.1 | Tehty Pulkkasen mukaiset muutokset, esim. kielilisäykset, uudet kaupungit ja muotoilumuutoksia. Ks. Pulkkasen sähköposti ja Excel-liite muutostoiveista. Korjattu dm³/s / m³/h laskentavirhe kennon hyötysuhteen laskennassa (syöttöarvo muuttuu kun kieli vaihtuu). | JK | 2024-09-10 | Airfi laskentaohjelma_6.1.xlsx
2024-10-25 | 7.0 beta 1 | Korjattu puolankielistä sanastoa kommenttiexcelin perusteella (25.9.2024 saatu). Lisätty alustava C-sarjan laskentaohjelma + koodiavain. Palautettu alustavana kommenteille, ei vielä kaikkia ominaisuuksia eikä patterimitoituksia tai SFPint-laskentaa. Korjattu Model 350 SFPint-laskennan hyötysuhdearvo (referenssi ilmavirran EN 308) | JK | 2024-10-25 | Airfi laskentaohjelma_v7.0 beta 1.xlsx
2024-11-28 | 7.0 beta 2 | Tehty Pulkkasen viestin mukaiset muutokset (excel + sähköposti 21.11.2024): mm. koodiavaimen jaksottelu ja kooditulostus viereen ja muita pieniä muutoksia koodiavaimen teksteihin. Poistettu C-sarjan SEC-laskenta (puhelinkeskustelu 26.11.2024). Lisätty SFPint-laskenta ja suodattimen vaikutus painehäviöihin. 350-kojeen SFP_int_limit -laskenta päivitetty (kiinteä arvot). | JK+JU | 2024-11-28 | Airfi laskentaohjelma_v7.0 beta 2.xlsx
2024-12-09 | 7.0 beta 3 | Lisätty koodiavaimen valintatulostus C-series -välilehdelle. C-sarjan kohde- ja suunnittelijan syöte ainoastaan C-selectioniin, josta haetaan C-series -välilehdelle. | JK | 2024-12-09 | Airfi laskentaohjelma_v7.0 beta 3.xlsx
2025-01-17 | 7.0 beta 4 | Lisätty patterimitoitus C-sarjaan, muokattu koodiavainta 7.1.2025 mailin mukaisesti (riviliitinvalinnan pakotukset koodin kohtien O, Q ja RR valintoihin). | JK+JU | 2025-01-17 | Airfi laskentaohjelma_v7.0 beta 4.xlsx
2025-01-28 | 7.1 | C-sarjan valintakoodi- ja mitoitusvälilehdet FIN/ENG. Sähköpostin 20.1.2025 mukaiset muutokset. | JK | 2025-01-30 | Airfi laskentaohjelma_v7.1
2025-04-16 | 7.2 | Lisätty uusi konemalli Model 53mini | JK | 2025-04-17 | Airfi laskentaohjelma_v7.2
2025-05-02 | 7.3 | Toteutettu Model 53minin keittiohituksen laskenta | JK | 2025-05-02 | Airfi laskentaohjelma_v7.3